SnapAI Comprehensive AC Diagnostic Guide All Issues · Diagnosis Steps · App Workflow · Decision Trees · Solutions Prepared by Mark Reyes — 20 years HVAC, Houston TX ¦ April 2026

# MASTER REFERENCE — All 19 Issues: Frequency, Confidence & Action

This table is the single-page command centre for every service call. Houston frequency percentages are based on 20 years of field data from Mark Reyes and reflect the share of professional residential service calls where each issue is a primary or contributing diagnosis. Percentages sum above 100% because a single call often involves more than one issue.

How to Read App Confidence Levels AUTO-CONFIRM: App makes the diagnosis independently — no tech interpretation needed. ASSISTED: App routes correctly and guides the check; tech reads the instrument and enters the value. PHASE 2 REQUIRED: App cannot confirm without mandatory readings gate, superheat/subcooling auto-calc, or thermal camera — these are on the Phase 2 roadmap. TECH JUDGMENT: Requires specialist knowledge, Manual J calculation, or equipment beyond current app scope. App flags the possibility; human must confirm.

| # | Issue | Severity | Houston % | App Confidence | Phase Needed | Remaining Action / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Dirty Air Filter | MEDIUM | 18–22% | AUTO-CONFIRM | Phase 1 ✅ | Photo + delta T. App flags if delta T <14°F. No remaining blockers. |
| 2 | Choking / Blockage | HIGH | 3–5% | PHASE 2 REQUIRED | Phase 2 🔧 | Needs mandatory readings gate (Task #9) for standing vs running pressure comparison. |
| 3 | Refrigerant Leak | CRITICAL | 20–25% | ASSISTED | Phase 1 ✅ | App calculates from entered pressures. Leak location still requires tech + detector. |
| 4 | TXV Failure | HIGH | 5–7% | PHASE 2 REQUIRED | Phase 2 🔧 | Superheat/subcooling auto-calc (Task #10) required to confirm stuck-closed vs stuck-open. |
| 5 | Power Faults | HIGH | 7–9% | AUTO-CONFIRM | Phase 1 ✅ | Voltage + 24V signal checks are binary. App confirms from entered values. |
| 6 | Capacitor Failure | CRITICAL | 35–40% (summer) | AUTO-CONFIRM | Phase 1 ✅ | MFD reading vs nameplate ±6% is binary. App calculates pass/fail automatically. |
| 7 | Contactor Failure | CRITICAL | 8–10% | AUTO-CONFIRM | Phase 1 ✅ | 24V at coil + voltage drop across contacts = binary. App confirms. |
| 8 | Compressor Health | CRITICAL | 4–6% | PHASE 2 REQUIRED | Phase 2 🔧 | Compression ratio calc (Task #10) needed. App flags high amp draw but cannot confirm valve wear alone. |
| 9 | Motor Failure | MEDIUM | 5–7% | AUTO-CONFIRM | Phase 1 ✅ | Amp draw vs nameplate FLA + bearing spin test. App calculates from entered values. |
| 10 | Drainage Issues | MEDIUM | 15–18% | AUTO-CONFIRM | Phase 1 ✅ | Level check + drain flow test. Photo of drain pan. App confirms. |
| 11 | PCB / Error Codes | HIGH | 4–6% | AUTO-CONFIRM | Phase 1 ✅ | Error code lookup + component tests. App routes from code to specific check. |
| 12 | Ductwork Leaks | MEDIUM | 12–15% | TECH JUDGMENT | Phase 2+ 🔬 | Register temp proxy is screening only. Blower door test required for definitive diagnosis. |
| 13 | Reversing Valve | HIGH | 2–3% | ASSISTED | Phase 1 ✅ | Solenoid resistance + click test. App confirms from entered values. |
| 14 | Dirty Coil | HIGH | 18–22% (spring peak) | ASSISTED | Phase 1 ✅ | YOLO detects blockage in photos. Water spray test result entered by tech. App confirms. |
| 15 | Fixed Orifice / Piston | HIGH | 8–10% (of applicable units) | PHASE 2 REQUIRED | Phase 2 🔧 | Stable superheat check requires auto-calc (Task #10). App routes correctly but cannot confirm sizing. |
| 16 | Loose Terminal / Wiring | CRITICAL | 10–12% | PHASE 2 REQUIRED | Phase 2 🔧 | Voltage drop check entered manually. Thermal camera (Phase 2) needed for definitive confirmation. |
| 17 | Refrigerant Overcharge | HIGH | 7–9% | PHASE 2 REQUIRED | Phase 2 🔧 | Requires simultaneous suction+discharge comparison + subcooling calc (Task #10) to distinguish from dirty coil. |
| 18 | System Undersizing | MEDIUM | 10–13% | TECH JUDGMENT | Phase 3 🔬 | Requires Manual J load calculation. App flags possibility only. Human engineer must confirm and size replacement. |
| 19 | Formicary Corrosion | HIGH | 4–6% | ASSISTED | Phase 1 ✅ | Electronic leak detector at coil face. App prompts the step. Tech interprets detector reading. |

| AUTO-CONFIRM 8 of 19 issues App diagnoses independently | ASSISTED 3 of 19 issues App guides, tech confirms value | PHASE 2 REQUIRED 6 of 19 issues Superheat calc / thermal cam needed | TECH JUDGMENT 2 of 19 issues Manual J or blower door required |
| --- | --- | --- | --- |

Phase 1 Launch Reality Check With Phase 1 live today: the app AUTO-CONFIRMs or ASSISTs on 11 of 19 issues — covering capacitor, contactor, power faults, gas leak, dirty filter, dirty coil, water drainage, PCB errors, motor failure, reversing valve, and formicary corrosion. These 11 issues account for roughly 70–75% of all Houston residential service calls by volume. Phase 2 (mandatory readings gate + superheat/subcooling auto-calc + thermal camera) unlocks 6 more cards and pushes coverage to 90%+ of all calls. The remaining 2 cards (ductwork, undersizing) require specialist equipment and will always need tech judgment.

# PART 1 — Master Diagnostic Decision Tree

Start every service call here. Follow the complaint the customer reported and work down the tree until you reach a confirmed diagnosis. Each terminal node links to the full issue card in Part 2.

|  | ▶ CUSTOMER COMPLAINT — What is the problem? |
| --- | --- |

|  | A NOT COOLING / WARM AIR |
| --- | --- |

|  | A1 Is the outdoor unit running? |
| --- | --- |

|  | → NO Go to Issue #5: AC Not Turning On / Power Faults |
| --- | --- |

|  | → YES Continue below ↓ |
| --- | --- |

|  | A2 Is airflow coming from indoor vents? |
| --- | --- |

|  | → NONE / WEAK Check air filter → Issue #1: Dirty Air Filter. Also check blower motor → Issue #9: Motor Failure. |
| --- | --- |

|  | → NORMAL Continue below ↓ |
| --- | --- |

|  | A3 Take suction & discharge pressure readings. Identify refrigerant type from serial number. |
| --- | --- |

|  | A3a Pressure normal when OFF, drops to 0 when ON → Issue #2: Choking/Blockage |
| --- | --- |

|  | A3b Pressure LOW both ON and OFF → Issue #3: Refrigerant Leak |
| --- | --- |

|  | A3c Pressure normal, superheat HIGH (>18°F) → Issue #4: TXV Stuck Closed / Restriction |
| --- | --- |

|  | A3d Pressure normal, superheat LOW (<6°F) → Issue #4: TXV Stuck Open / Overcharge |
| --- | --- |

|  | A3e Suction HIGH, delta T low — outdoor fan not moving air → Issue #9: Condenser Fan Motor |
| --- | --- |

|  | A3f Compressor not starting, clicking or humming → Issue #6: Capacitor Failure |
| --- | --- |

|  | A3g Compressor amp draw >115% of nameplate RLA → Issue #8: Compressor Health |
| --- | --- |

|  | B WATER DRIPPING FROM INDOOR UNIT |
| --- | --- |

|  | B1 Is there ice on the refrigerant lines or indoor coil? |
| --- | --- |

|  | → YES — ICE PRESENT Check air filter first (Issue #1). If clean, check refrigerant — likely Issue #3: Refrigerant Leak (low charge = frozen coil) |
| --- | --- |

|  | → NO ICE Continue below ↓ |
| --- | --- |

|  | B2 Is the unit level? Check with spirit level. |
| --- | --- |

|  | → UNIT NOT LEVEL Issue #10: Installation / Level Problem — shim and re-level |
| --- | --- |

|  | → UNIT LEVEL Issue #10: Drainage Blockage — flush condensate drain line |
| --- | --- |

|  | C UNIT NOT TURNING ON AT ALL |
| --- | --- |

|  | C1 Is there 240V at the wall disconnect? |
| --- | --- |

|  | → NO POWER Check main breaker panel. Not an AC issue — electrical supply problem. |
| --- | --- |

|  | → POWER OK Continue below ↓ |
| --- | --- |

|  | C2 Does the indoor unit turn on but outdoor does not? |
| --- | --- |

|  | → YES Check contactor (Issue #7). Check capacitor (Issue #6). Check disconnect fuse. |
| --- | --- |

|  | → NEITHER TURNS ON Check thermostat signal, indoor PCB fuse, communication wire → Issue #5: Power Faults, Issue #11: PCB Error |
| --- | --- |

|  | D MAKING UNUSUAL NOISE |
| --- | --- |

|  | D1 Where is the noise coming from? |
| --- | --- |

|  | → INDOOR UNIT: rattling/clanking Blower wheel hitting casing → Issue #9: Motor/Fan Alignment |
| --- | --- |

|  | → INDOOR UNIT: squealing Blower motor bearing failure → Issue #9: Motor Replacement |
| --- | --- |

|  | → OUTDOOR: clicking on/off rapidly Contactor chattering → Issue #7: Contactor Failure |
| --- | --- |

|  | → OUTDOOR: loud hum, won't start Capacitor failure → Issue #6: Capacitor Failure |
| --- | --- |

|  | → OUTDOOR: grinding/loud knocking Fan blade damage or compressor mechanical failure → Issue #8 or #9 |
| --- | --- |

|  | E HIGH ELECTRIC BILL / UNIT RUNS CONSTANTLY |
| --- | --- |

|  | E1 Check air filter first |
| --- | --- |

|  | → DIRTY FILTER Issue #1: Replace filter. Retest delta T. |
| --- | --- |

|  | E2 Check delta T (supply vs return). Target: 18–22°F |
| --- | --- |

|  | → DELTA T LOW (<14°F) Refrigerant issue (Issue #3) or coil issue |
| --- | --- |

|  | E3 Check register temperatures across all rooms |
| --- | --- |

|  | → SOME ROOMS MUCH WARMER Ductwork leak — Issue #12: Ductwork Assessment |
| --- | --- |

|  | E4 Check unit age from serial number |
| --- | --- |

|  | → UNIT OVER 12 YEARS OLD SEER degradation. Discuss system replacement economics. Issue #8. |
| --- | --- |

|  | F ERROR CODE ON DISPLAY |
| --- | --- |

|  | F1 Read the error code and identify category |
| --- | --- |

|  | → Communication error (E6, E1, etc.) Check 4-core signal wire continuity → Issue #11: PCB/Electronic Faults |
| --- | --- |

|  | → Sensor fault (F1, F3, etc.) Test thermistor resistance → Issue #11: Sensor Replacement |
| --- | --- |

|  | → IPM / Power module Check heat sink paste, module continuity → Issue #11: PCB Repair |
| --- | --- |

|  | → Pressure protection (high/low pressure) Go to Branch A (refrigerant fault) — pressure switch tripped the protection |
| --- | --- |

|  | G HEATING NOT WORKING (HEAT PUMP SYSTEMS) |
| --- | --- |

|  | G1 Is the reversing valve switching? (listen for a click when switching modes) |
| --- | --- |

|  | → NO CLICK / STUCK Issue #13: Reversing Valve Failure |
| --- | --- |

|  | → CLICK HEARD Check defrost cycle, refrigerant charge in heating mode |
| --- | --- |

|  | H HIGH DISCHARGE PRESSURE — SYSTEM COOLING BUT STRUGGLING |
| --- | --- |

|  | H1 Spray condenser coil with water. Does discharge pressure drop within 60 seconds? |
| --- | --- |

|  | → YES — PRESSURE DROPS Issue #14: Dirty Condenser Coil — blockage was reducing heat rejection |
| --- | --- |

|  | → NO CHANGE Pressure issue is refrigerant-side — go back to Branch A3 |
| --- | --- |

|  | H2 Check evaporator coil access. Is coil surface grey/black with debris? |
| --- | --- |

|  | → YES — COIL BLOCKED Issue #14: Dirty Evaporator Coil — clean before any refrigerant diagnosis |
| --- | --- |

|  | I INTERMITTENT FAULTS — UNIT FAILS AND RESTARTS RANDOMLY |
| --- | --- |

|  | I1 Does fault occur more often when unit has been running 20+ minutes (heat soak)? |
| --- | --- |

|  | → YES Issue #16: Loose Terminal / Wiring Fault — thermal expansion causes intermittent arc |
| --- | --- |

|  | I2 Check all compressor, contactor, and disconnect terminals with unit off. Any discoloration? |
| --- | --- |

|  | → BURNT / DISCOLORED TERMINAL Issue #16: Loose Terminal — tighten, clean, or replace terminal block before any other diagnosis |
| --- | --- |

|  | → ALL TERMINALS CLEAN Check capacitor (Issue #6), PCB error code (Issue #11), then return to main tree |
| --- | --- |

|  | J SYSTEM COOLING BUT PRESSURES BOTH ABNORMALLY HIGH |
| --- | --- |

|  | J1 Is the condenser coil clean? Run water spray test (Branch H first) |
| --- | --- |

|  | → COIL CLEAN, BOTH PSI STILL HIGH Issue #17: Refrigerant Overcharge — suction AND discharge both above normal = overcharge signature |
| --- | --- |

|  | J2 Was refrigerant added to this system in the last 12 months without recovery? |
| --- | --- |

|  | → YES — REFRIGERANT ADDED Likely overcharge. Recover to correct weight. Do NOT add more refrigerant. |
| --- | --- |

|  | J3 Unit passes all 16 checks but still cannot hit setpoint after 30 min on 95°F day? |
| --- | --- |

|  | → ALL CHECKS PASS, STILL FAILING Issue #18: System Undersizing / Wrong Tonnage — request Manual J assessment |
| --- | --- |

# PART 2 — Individual Issue Cards

Each card covers: symptoms, required photos, measurements, how the app handles it, and the three estimate options.

| 1. Dirty / Clogged Air Filter | MEDIUM |
| --- | --- |

🔍 SYMPTOMS / WHAT TECH SEES - Customer complains AC is not cooling well or running constantly - Ice forming on indoor coil or refrigerant lines - Reduced or no airflow from supply vents - Higher than normal electric bills - Return air temperature drop is less than 14°F

| 📷 PHOTOS TO TAKE - Indoor unit — return air grille (show filter location) - Filter itself — pull out and photograph against light to show blockage - Indoor coil if icing is visible | 📊 READINGS / MEASUREMENTS - Delta T: supply temp vs return temp (target 18–22°F, below 14°F = restricted airflow) - Suction pressure (will be LOW if coil is icing from restricted airflow) - Blower motor amp draw if airflow feels restricted but filter looks clean |
| --- | --- |

📱 HOW THE APP HANDLES THIS Step 1: App prompts: 'Customer says not cooling — check air filter first. Photograph the return grille and the filter.' Step 2: App captures filter photo and asks: 'Is the filter visibly clogged?' Yes/No. Yes → immediately flags as likely root cause. Step 3: App records delta T readings. If delta T <14°F, confirms airflow restriction. Step 4: App notes whether coil icing is present (links to refrigerant check if icing persists after filter change). Step 5: Estimate generated: filter replacement + cleaning service.

| ✅ OPTION A — GOOD - Replace filter ($5–20 part) - Clean return grille - Retest delta T | 🔧 OPTION B — BETTER - Replace filter - Full indoor coil cleaning with coil cleaner - Check and clean blower wheel | ⭐ OPTION C — BEST - Filter replacement - Full system cleaning including coil, blower, drain pan - Install 4-inch media filter for longer change intervals |
| --- | --- | --- |

🔔 LIFECYCLE / PREVENTION Filter life: 1–3 months (standard 1-inch). 4-inch media filters last 6–12 months. App should set a proactive reminder at 60 days for standard, 9 months for media filters.

| 2. Choking / Blockage (Cap Tube or Metering Device Restriction) | HIGH |
| --- | --- |

🔍 SYMPTOMS / WHAT TECH SEES - No cooling despite compressor running - Pressure gauge reads normal or high when unit is OFF (standing pressure) - When unit turns ON, suction pressure drops rapidly to 0 PSI or goes into vacuum - Ice may form at the point of restriction (just before the metering device) - Often follows a poor installation or pipe soldering job

| 📷 PHOTOS TO TAKE - Gauge manifold connected to service ports (photo showing standing pressure reading) - Refrigerant lines — close-up of the point of restriction or metering device location - Outdoor unit service area showing both gauges after unit starts | 📊 READINGS / MEASUREMENTS - Standing pressure (unit OFF): R-410A ~120–130 PSI, R-22 ~65–80 PSI, R-32 ~130 PSI - Suction pressure (unit ON): drops below 0 PSI rapidly = confirmed blockage - Suction pressure (unit ON): stays normal = not a blockage - Discharge pressure - Delta T across the indoor coil |
| --- | --- |

📱 HOW THE APP HANDLES THIS Step 1: App intake: 'Customer says not cooling.' Prompts for outdoor unit running check. Step 2: App prompts: 'Connect gauge manifold. Record standing pressure (unit OFF).' Records the value. Step 3: App prompts: 'Turn unit on. Record suction pressure after 2 minutes.' If it drops sharply to 0 or below, app flags: CHOKING SUSPECTED. Step 4: App confirms with delta T reading — near-zero delta T with pressure collapse = confirmed blockage. Step 5: App generates estimate: system flush + component replacement.

| ✅ OPTION A — GOOD - Nitrogen flush of the system - Replace cap tube or metering orifice - Replace filter drier - Deep vacuum (min 300 microns) + recharge to spec | 🔧 OPTION B — BETTER - Full system flush with nitrogen - Replace metering device + filter drier - Replace liquid line if contaminated - Deep vacuum + recharge | ⭐ OPTION C — BEST - Full system flush - Replace metering device, filter drier, and liquid line - Pressure test at 400 PSI before recharge - Deep vacuum to 250 microns, recharge to nameplate weight |
| --- | --- | --- |

🔔 LIFECYCLE / PREVENTION Prevention: proper nitrogen purge during pipe brazing prevents contamination. Moisture in the system from poor vacuum is the main cause. App should flag systems with repeated choking history for mandatory vacuum verification at every service.

| 3. Low Refrigerant / Gas Leak | CRITICAL |
| --- | --- |

🔍 SYMPTOMS / WHAT TECH SEES - Not cooling or very weak cooling - Ice forming on the suction line (thin copper pipe) or indoor coil - Suction pressure low BOTH when unit is off AND running - Oily residue around pipe joints or flare fittings - Minor leak: cooling gradually degrades over weeks. Major leak: no cooling within 30 minutes - R-22 systems: sweet chemical smell sometimes reported

| 📷 PHOTOS TO TAKE - Suction line close-up showing ice or oily residue - All pipe joints and flare fittings (look for oily staining) - Outdoor unit service ports showing gauge readings - Indoor coil if accessible — frost patterns indicate low charge - Any visible corrosion on copper lines | 📊 READINGS / MEASUREMENTS - Standing pressure (unit OFF): significantly below normal = low charge - Suction pressure (unit ON): below normal operating range - Superheat: HIGH (above 18°F) = undercharged - Sub-cooling: NEAR ZERO = undercharged - Electronic leak detector reading at all joints and coil bends |
| --- | --- |

📱 HOW THE APP HANDLES THIS Step 1: App prompts: 'Take gauge readings with unit OFF and ON.' Records both. Step 2: App calculates: is standing pressure below normal for this refrigerant type? Auto-detected from serial number. Step 3: App prompts: 'Check for oily residue at all fittings. Photograph any found.' Step 4: App prompts: 'Enter suction line temperature for superheat calculation.' Calculates superheat automatically. Step 5: App flags: REFRIGERANT LEAK SUSPECTED. Prompts leak detection step. Step 6: Estimate generated: leak location, repair, and recharge. R-22 systems flagged separately with replacement recommendation.

| ✅ OPTION A — GOOD - Locate and braze/repair the leak (if accessible) - Replace filter drier - Pressure test at 400 PSI - Deep vacuum + recharge to nameplate weight | 🔧 OPTION B — BETTER - Locate and repair leak - Replace affected coil section or fitting - Replace filter drier + liquid line filter - Pressure test, deep vacuum, recharge + leak verification dye | ⭐ OPTION C — BEST - Full leak repair or coil replacement if coil is leaking - Complete system flush if contaminated - New filter drier - Nitrogen pressure test, deep vacuum to 250 microns, precision recharge by weight + leak check at 30 days |
| --- | --- | --- |

🔔 LIFECYCLE / PREVENTION R-22 ALERT: App auto-detects R-22 from serial number (pre-2010 units). For R-22 leaks, app must flag: recharge cost is $80–120/lb vs $12–18/lb for R-410A. For any R-22 leak, Option C should always be full system replacement, not recharge.

| 4. TXV Failure (Thermostatic Expansion Valve) | HIGH |
| --- | --- |

🔍 SYMPTOMS / WHAT TECH SEES - Not cooling despite normal or high suction pressure - Suction line may be sweating heavily (TXV stuck open) or very warm (TXV stuck closed) - Suction pressure swings up and down repeatedly (TXV hunting) - Superheat either very high (>20°F, stuck closed) or very low (<4°F, stuck open) - Compressor may trip on high pressure or low pressure safety

| 📷 PHOTOS TO TAKE - TXV body and bulb location on the suction line (close-up) - Suction line temperature probe location - Gauge manifold showing suction and discharge simultaneously - Indoor coil access panel (show whether coil looks flooded or starved) | 📊 READINGS / MEASUREMENTS - Suction pressure: note whether stable or swinging - Discharge pressure - Suction line temperature at TXV bulb location - Superheat calculation (suction line temp minus saturation temp at suction PSI): >18°F = stuck closed, <5°F = stuck open, fluctuating = hunting - Subcooling at liquid line |
| --- | --- |

📱 HOW THE APP HANDLES THIS Step 1: App prompts: gauge readings + suction line temp at TXV bulb. Step 2: App calculates superheat automatically. If superheat >18°F with normal or high discharge pressure, app flags: TXV STUCK CLOSED. Step 3: If superheat <5°F, app flags: TXV STUCK OPEN or OVERCHARGED — check subcooling to distinguish. Step 4: If suction pressure is cycling repeatedly, app flags: TXV HUNTING — likely debris in valve seat or bulb charge lost. Step 5: App generates estimate: TXV replacement. Notes whether refrigerant recovery is needed.

| ✅ OPTION A — GOOD - TXV replacement - Filter drier replacement - System recharge to spec | 🔧 OPTION B — BETTER - TXV replacement with upgraded model - Filter drier replacement - Flush liquid line - Recharge by weight + verify superheat after | ⭐ OPTION C — BEST - TXV replacement - Full coil inspection (flooded coil can damage scroll compressor) - Filter drier + liquid line filter - Recharge + verify superheat and subcooling at spec |
| --- | --- | --- |

🔔 LIFECYCLE / PREVENTION TXV hunting is often caused by dirty refrigerant or moisture. A system with a failed TXV should always get a new filter drier. App should flag: if compressor was running with low superheat for extended period, check compressor amp draw — flood-back can score scroll compressor surfaces. IMPORTANT — FIXED ORIFICE / PISTON SYSTEMS: Many builder-grade Houston units (Lennox, Carrier, Goodman 2005–2015) use a fixed orifice piston instead of a TXV. Diagnosis is different: a worn or wrong-size piston causes permanently low superheat (stuck-open-equivalent) or high superheat (wrong orifice size), but without the hunting signature. Replacement is a simple orifice swap — no valve body work. App must ask at Step 1: 'Is this system TXV or fixed orifice?' and route accordingly. See Issue #15 for full fixed orifice card.

| 5. AC Not Turning On / Power Faults | HIGH |
| --- | --- |

🔍 SYMPTOMS / WHAT TECH SEES - Indoor unit does not respond to thermostat - No lights or display on indoor unit - Indoor on but outdoor unit completely silent - Breaker trips repeatedly when AC starts - Outdoor unit hums briefly then shuts off

| 📷 PHOTOS TO TAKE - Main disconnect at outdoor unit (show visible fuse/breaker condition) - Indoor PCB — close-up of fuse and relay - Thermostat display and wiring connections - Contactor — show contact surface condition - Any burnt or melted wiring visible | 📊 READINGS / MEASUREMENTS - Voltage at wall disconnect: must be 220–240V (US: 240V) - Voltage at compressor terminals under load - 24V signal from thermostat at contactor coil terminals - Contactor coil resistance (should be 8–20 ohms) - Blower motor amp draw (indoor on, outdoor not responding) |
| --- | --- |

📱 HOW THE APP HANDLES THIS Step 1: App prompts: 'Does indoor unit power on?' No → Check thermostat and indoor fuse. Step 2: App prompts: 'Does outdoor unit receive power?' Check disconnect and run capacitor. Step 3: App prompts: 'Is 24V present at contactor coil terminals?' If yes but contactor not closing → Issue #7 Contactor. Step 4: App prompts: 'Is voltage at compressor terminals above 220V?' If no → brownout or wiring issue. Step 5: App generates estimate based on confirmed failed component.

| ✅ OPTION A — GOOD - Replace blown fuse or reset breaker - If tripping: identify root cause component before resetting | 🔧 OPTION B — BETTER - Replace failed component (contactor, capacitor, or PCB fuse) - Test all electrical connections for corrosion - Verify voltage at all terminals | ⭐ OPTION C — BEST - Full electrical inspection of outdoor unit - Tighten all terminals, check wire gauges - Install surge protector on the system - Verify disconnect rating matches equipment nameplate |
| --- | --- | --- |

🔔 LIFECYCLE / PREVENTION Houston voltage brownouts during summer peak demand (3–6pm) are common. Units that trip repeatedly may have a voltage issue, not an equipment issue. App should capture voltage reading and flag if below 215V.

| 6. Capacitor Failure | CRITICAL |
| --- | --- |

🔍 SYMPTOMS / WHAT TECH SEES - Outdoor unit hums loudly but compressor does not start - Fan spins slowly or only starts if given a manual push - Unit trips breaker on startup - Compressor cycling on thermal overload - Common on Houston calls: 35–40% of summer service calls

| 📷 PHOTOS TO TAKE - Capacitor — remove panel and photograph the capacitor (look for bulging top, leaking oil) - Capacitor rating label close-up showing MFD and VAC ratings - Contactor area to rule out simultaneous failure | 📊 READINGS / MEASUREMENTS - Capacitor microfarad reading with capacitor tester: compare to nameplate rating. Tolerance is ±6%. A 35 MFD cap reading below 32.9 MFD is failed. - Compressor amp draw (LRA on startup vs RLA running) - Fan motor amp draw - Voltage at capacitor terminals |
| --- | --- |

📱 HOW THE APP HANDLES THIS Step 1: App prompts complaint 'outdoor not starting / humming' → immediately routes to capacitor check. Step 2: App prompts: 'Remove capacitor. Read microfarad with capacitor tester. Enter reading and nameplate rating.' Step 3: App calculates: is reading within ±6% of nameplate? If no → CAPACITOR FAILED confirmed. Step 4: App prompts photo of capacitor for visual inspection (bulging top = confirmed failed). Step 5: App generates estimate: capacitor replacement. Dual-run or two separate capacitors depending on system.

| ✅ OPTION A — GOOD - Replace capacitor with correct MFD/VAC rating - Verify fan and compressor start properly after replacement | 🔧 OPTION B — BETTER - Replace capacitor - Test compressor amp draw after — if still high, check for other damage - Clean outdoor coil while panel is open | ⭐ OPTION C — BEST - Replace capacitor - Full electrical inspection — contactor, wiring, disconnect - Install hard start kit if compressor shows high LRA - Clean condenser coil |
| --- | --- | --- |

🔔 LIFECYCLE / PREVENTION Capacitor life: 5–8 years in Houston heat. App lifecycle tracking: flag any system over 6 years old for a proactive capacitor check every spring before cooling season. A failed capacitor left too long will destroy the compressor motor windings.

| 7. Contactor Failure | CRITICAL |
| --- | --- |

🔍 SYMPTOMS / WHAT TECH SEES - Outdoor unit does not turn on despite 24V signal from thermostat - Loud chattering or buzzing from outdoor unit contactor - Contact points visibly burnt or pitted - System turns on and off rapidly (short cycling at the contactor) - 24V present at coil but contactor not closing

| 📷 PHOTOS TO TAKE - Contactor close-up — show contact surface condition (pitting, burning, carbon deposits) - Control wiring connections at contactor - Multimeter reading across contactor contacts | 📊 READINGS / MEASUREMENTS - 24V across contactor coil terminals: must be present when thermostat calls for cooling - Voltage drop across closed contact points: should be 0V when closed, line voltage when open - Contact surface resistance: any measurable resistance across closed contacts = bad contacts - Coil resistance: 8–20 ohms is normal |
| --- | --- |

📱 HOW THE APP HANDLES THIS Step 1: App prompts: 'Is 24V at contactor coil terminals?' If yes and unit not starting → contactor check. Step 2: App prompts: 'Is voltage passing through the contacts to the compressor?' If 24V at coil but no voltage at load side → CONTACTOR FAILED. Step 3: App prompts photo of contact surface — heavy pitting or burning confirms replacement. Step 4: App generates estimate: contactor replacement ($20–40 part, 20-minute repair).

| ✅ OPTION A — GOOD - Replace contactor with matching amp rating and coil voltage - Verify system starts normally after | 🔧 OPTION B — BETTER - Replace contactor - Inspect and clean all wiring connections - Check capacitor simultaneously (often fail together in summer) | ⭐ OPTION C — BEST - Replace contactor - Replace capacitor as preventive measure - Install surge protector - Full electrical inspection |
| --- | --- | --- |

🔔 LIFECYCLE / PREVENTION Contactors in Houston last 5–10 years. The summer heat and frequent on/off cycling accelerates contact erosion. App: any system over 7 years old should get a contactor inspection every spring. If a capacitor failed, always check the contactor simultaneously.

| 8. Compressor Health / Failure | CRITICAL |
| --- | --- |

🔍 SYMPTOMS / WHAT TECH SEES - Unit runs but delta T (cooling output) very low despite correct refrigerant charge - Compressor amp draw significantly above nameplate RLA - High suction pressure with low discharge pressure (low compression ratio = worn valves) - Compressor trips on thermal overload repeatedly - Compressor makes grinding, clanking, or rattling sounds internally - Unit over 12 years old in Houston heat

| 📷 PHOTOS TO TAKE - Compressor body — look for oily staining, cracks, or impact damage - Gauge manifold showing suction and discharge simultaneously - Compressor wiring terminals and run capacitor - Serial number plate for age determination | 📊 READINGS / MEASUREMENTS - Compressor amp draw (L1 and L2): compare to nameplate RLA. Over 115% of RLA = failing - Suction and discharge pressures under load: calculate compression ratio. R-410A target 2.5–3.5:1. Lower = worn valves - Voltage at compressor terminals under load - Superheat and subcooling to confirm refrigerant charge is not the issue - Megohm test on compressor windings (ground fault check) |
| --- | --- |

📱 HOW THE APP HANDLES THIS Step 1: App prompts pressure and amp readings if compressor is suspected. Step 2: App calculates compression ratio automatically. If below 2.0:1 with correct charge → COMPRESSOR EFFICIENCY LOW. Step 3: App flags unit age from serial decoder. If over 12 years, system replacement economics are presented. Step 4: App generates two parallel estimates: compressor replacement vs full system replacement with ROI comparison. Step 5: App shows 5-year cost comparison: repair vs replace, including SEER savings.

| ✅ OPTION A — GOOD - Hard start kit if compressor struggles to start but is otherwise healthy - Verify capacitor and contactor first (cheaper fixes) | 🔧 OPTION B — BETTER - Compressor replacement by certified tech - System flush after compressor replacement - Recharge to spec + verify operation | ⭐ OPTION C — BEST - Full system replacement (condenser + air handler + metering device + lineset flush) - Higher SEER unit for energy savings - Proper sizing calculation (Manual J) for the home |
| --- | --- | --- |

🔔 LIFECYCLE / PREVENTION Compressor life in Houston: 10–15 years. For any compressor over 10 years old, Option C (full system) should be presented as the financially smart choice. App: calculate remaining useful life vs replacement cost + SEER savings. If repair cost exceeds 50% of replacement cost, replacement is always Option C.

| 9. Motor Failure (Blower or Condenser Fan) | MEDIUM |
| --- | --- |

🔍 SYMPTOMS / WHAT TECH SEES - Loud grinding, squealing, or rattling from the unit - Indoor unit running but no airflow (blower motor failure) - Outdoor unit running but condenser getting very hot (fan motor failure → high discharge pressure) - Fan blade hitting casing (rattle or clank on every revolution) - Motor runs briefly then shuts off on thermal overload

| 📷 PHOTOS TO TAKE - Motor nameplate — photograph brand, HP, RPM, and capacitor spec - Fan blade — check for cracks, missing sections, or bend - Motor mounting bracket condition - Indoor blower wheel if accessible — look for debris or out-of-balance | 📊 READINGS / MEASUREMENTS - Motor amp draw vs nameplate FLA: above nameplate = bad bearings or restriction - Capacitor reading for the motor (fan and blower have separate capacitors) - Discharge pressure (condenser fan failure causes high discharge pressure) - Delta T across indoor coil (blower failure = low delta T) - Bearing resistance: spin the motor by hand — rough = bad bearings |
| --- | --- |

📱 HOW THE APP HANDLES THIS Step 1: App routes to motor check based on noise complaint or high discharge pressure. Step 2: App prompts: 'Spin the fan/blower motor by hand with power off. Is rotation smooth?' Rough = bearing failure. Step 3: App prompts amp draw reading and nameplate FLA. Calculates if motor is overloaded. Step 4: App prompts capacitor check for the affected motor simultaneously. Step 5: App generates estimate: motor replacement. Notes brand and model for parts ordering.

| ✅ OPTION A — GOOD - Replace failed motor with exact match (brand, HP, RPM, shaft size) - Replace motor run capacitor simultaneously | 🔧 OPTION B — BETTER - Replace motor and capacitor - Check and realign fan blade or blower wheel - Verify amp draw after replacement | ⭐ OPTION C — BEST - Replace motor and capacitor - Full inspection of wiring and connections - Clean coil or blower wheel while unit is open - Verify system operation through full cooling cycle |
| --- | --- | --- |

🔔 LIFECYCLE / PREVENTION Blower motor life: 12–20 years. Condenser fan motor life: 10–15 years in Houston heat. App lifecycle tracking: flag outdoor fan motors over 10 years for annual amp draw check every spring.

| 10. Water Leakage / Drainage Issues | MEDIUM |
| --- | --- |

🔍 SYMPTOMS / WHAT TECH SEES - Water dripping from indoor unit onto ceiling or floor - Standing water in the drain pan - Algae or slime visible in drain line or pan - Musty or mildew smell from vents - Unit may shut off on float switch if equipped

| 📷 PHOTOS TO TAKE - Drain pan — show standing water level and any algae growth - Condensate drain line exit point — show if blocked or dripping freely - Indoor unit level check — photograph with spirit level - Evaporator coil if visible — check for ice (indicates refrigerant issue, not drainage) | 📊 READINGS / MEASUREMENTS - Delta T — confirm system is cooling normally (rules out icing from low refrigerant) - Airflow check — restricted airflow causes icing which then overflows drain pan - Spirit level reading on the unit — must tilt slightly toward drain hole - Drain flow test — pour water into drain pan, verify it exits within 60 seconds |
| --- | --- |

📱 HOW THE APP HANDLES THIS Step 1: App prompts: 'Is there ice on the coil or suction line?' Yes → routes to refrigerant/airflow check first. Step 2: App prompts: 'Is the unit level?' Tech enters spirit level reading. App flags if not level. Step 3: App prompts: 'Pour 1 cup water into drain pan. Does it drain within 60 seconds?' No → DRAINAGE BLOCKED. Step 4: App photos: drain pan and drain line exit. App generates estimate: drain clearing + treatment.

| ✅ OPTION A — GOOD - Flush drain line with wet-vac or nitrogen - Clean drain pan with antimicrobial solution - Install algae prevention tablet in drain pan | 🔧 OPTION B — BETTER - Flush and clear drain line - Clean drain pan - Check and clean the condensate pump if present - Level the unit if needed | ⭐ OPTION C — BEST - Full drain system cleaning - Install primary and secondary drain with float switch - Add algae prevention treatment - Re-level unit if needed - Check that secondary drain exits to visible location (for early warning) |
| --- | --- | --- |

🔔 LIFECYCLE / PREVENTION Houston's humidity means condensate drain blockage is one of the most common calls. App reminder: recommend annual drain flush at every spring tune-up. A float switch that shuts off the system before overflow is a $40 add-on that prevents expensive ceiling damage — always present as an option.

| 11. PCB / Electronic Faults and Error Codes | HIGH |
| --- | --- |

🔍 SYMPTOMS / WHAT TECH SEES - Error code displayed on indoor unit or remote - Unit shuts down repeatedly and restarts - Indoor communicates, outdoor does not respond (or vice versa) - Sensor reading errors causing incorrect operation - IPM or power module protection shutting system down

| 📷 PHOTOS TO TAKE - Error code display — clear photo of the code shown - PCB board — look for burn marks, swollen capacitors, gecko/pest damage - Communication wire at both indoor and outdoor terminal blocks - Fuse on PCB — check for visibly blown fuse | 📊 READINGS / MEASUREMENTS - Error code: record the exact alphanumeric code and look up in manufacturer service manual - Communication wire continuity: pin 1 to pin 1 across indoor/outdoor (L, N, signal, ground) - Thermistor resistance: room sensor ~10kΩ at 77°F, coil sensor varies by manufacturer - Fuse continuity: 0Ω = good, OL = blown - IPM module: check for shorted legs with diode test mode |
| --- | --- |

📱 HOW THE APP HANDLES THIS Step 1: App prompts: 'Enter error code shown on display.' App looks up code in its database and returns the fault category. Step 2: App routes to specific check based on code type: communication → wire check. Sensor → thermistor test. IPM → board inspection. Step 3: App prompts photos of PCB and communication terminals. Step 4: App generates estimate: component replacement or PCB repair referral. Step 5: App flags gecko/pest damage as preventable with outdoor unit screening.

| ✅ OPTION A — GOOD - Replace the specific failed component (sensor, fuse, relay) - Clear error code and test operation | 🔧 OPTION B — BETTER - Replace failed component - Inspect all PCB components for secondary damage - Check wiring harness for rodent or pest damage | ⭐ OPTION C — BEST - Replace PCB if multiple components failed or if board is burnt - Install pest screening on outdoor unit - Full system test after replacement |
| --- | --- | --- |

🔔 LIFECYCLE / PREVENTION PCB failures are often caused by lightning strikes, power surges, or pests. App: recommend surge protection installation for any system in lightning-prone areas (all of Houston). Annual visual PCB inspection for pest damage should be part of the maintenance checklist.

| 12. Ductwork Leaks / Airflow Distribution Problems | MEDIUM |
| --- | --- |

🔍 SYMPTOMS / WHAT TECH SEES - Some rooms significantly warmer than others despite the AC running normally - Unit runs constantly but cannot maintain set temperature - Register airflow feels weak at far rooms but strong near the air handler - Electric bill higher than expected for the system size - Unit passes all refrigerant and electrical checks but cooling is still inadequate

| 📷 PHOTOS TO TAKE - Air handler return and supply plenum — look for visible gaps or disconnected ducts - Supply registers in problem rooms — photograph with anemometer or tissue test - Attic access if possible — look for disconnected or collapsed flex duct runs - Return air grille — check for unbalanced return vs supply | 📊 READINGS / MEASUREMENTS - Supply temperature at each register: enter into app. All should be within 2–3°F of each other. Large variation = duct leak to that zone. - Delta T across air handler: supply temp vs return temp. Should be 18–22°F. Normal here but low at far registers = duct leak. - Return air static pressure if manometer available - Airflow volume (CFM) at each register — simplified: tissue test, note if tissue barely deflects |
| --- | --- |

📱 HOW THE APP HANDLES THIS Step 1: App prompts: 'Record supply temperature at each register.' If one room reads significantly higher supply temp or lower flow → flags duct leak to that zone. Step 2: App calculates temperature consistency score across all registers entered. Step 3: App prompts photos of visible ductwork. Step 4: App generates estimate: duct sealing or repair. Aeroseal as a best-option recommendation.

| ✅ OPTION A — GOOD - Seal visible duct connections with mastic or metal tape (no duct tape) - Insulate any duct runs in unconditioned attic space | 🔧 OPTION B — BETTER - Locate and seal all accessible duct leaks - Add insulation to attic duct runs - Balance registers — adjust dampers for even distribution | ⭐ OPTION C — BEST - Professional duct leakage test (blower door + duct pressurization) - Aeroseal duct sealing (seals from inside, reaches inaccessible leaks) - Full duct rebalancing after sealing |
| --- | --- | --- |

🔔 LIFECYCLE / PREVENTION Mark estimates 25–30% of Houston 'AC not keeping up' calls have ductwork as a primary contributor. App should always include a duct check in the diagnostic tree for any complaint of uneven cooling or a unit that runs constantly despite good refrigerant and electrical health.

| 13. Reversing Valve Failure (Heat Pump Systems Only) | HIGH |
| --- | --- |

🔍 SYMPTOMS / WHAT TECH SEES - Heat pump blows warm air in cooling mode or cold air in heating mode - Unit cools on heating setting or heats on cooling setting (valve stuck in one position) - No click sound heard when switching between heating and cooling mode - System operates in one mode perfectly but not the other

| 📷 PHOTOS TO TAKE - Reversing valve body — located on outdoor unit refrigerant lines (D-shaped valve with 4 pipe connections) - Solenoid coil on reversing valve — check for burnt appearance - Suction and discharge line temperatures in both modes | 📊 READINGS / MEASUREMENTS - Solenoid coil continuity: should read 8–30Ω depending on manufacturer. Open circuit = failed solenoid. - Voltage at solenoid: 24V should be present when energized - Suction and discharge pressures in both cooling and heating mode: if pressures identical = valve not shifting - Temperature differential across valve ports |
| --- | --- |

📱 HOW THE APP HANDLES THIS Step 1: App complaint intake: 'Heating not working' or 'Cools in wrong mode.' Step 2: App prompts: 'Is this a heat pump system?' Yes → routes to reversing valve branch. Step 3: App prompts: 'Do you hear a click when switching from cooling to heating on the thermostat?' No click = valve not shifting. Step 4: App prompts solenoid coil resistance reading. Calculates pass/fail. Step 5: App generates estimate: solenoid coil replacement (if valve body is good) or full reversing valve replacement.

| ✅ OPTION A — GOOD - Replace solenoid coil only if coil is failed but valve body shifts freely (rare) - Verify valve shifts after coil replacement | 🔧 OPTION B — BETTER - Replace full reversing valve assembly - Recover refrigerant, braze new valve, recharge to spec | ⭐ OPTION C — BEST - Replace reversing valve - Full system inspection — check if stuck valve caused compressor damage from liquid slugging - Recharge + verify operation in both heating and cooling modes |
| --- | --- | --- |

🔔 LIFECYCLE / PREVENTION Reversing valve failures are not common but are often misdiagnosed as refrigerant issues because the pressure symptoms vary by which position the valve is stuck in. App should always flag heat pump status from serial number and include reversing valve in the diagnostic tree for any heat pump cooling or heating complaint.

| 14. Dirty Evaporator or Condenser Coil | HIGH |
| --- | --- |

🔍 SYMPTOMS / WHAT TECH SEES - High discharge pressure despite normal refrigerant charge - Unit cools but struggles — runs constantly and cannot hit setpoint - Delta T (supply vs return) lower than expected despite correct pressures - Condenser coil visibly clogged with cottonwood, leaves, grass clippings, or pet hair - Evaporator coil grey or black with mould, dust, or debris blocking fins - Ice forming on evaporator coil (restricted airflow through dirty coil) - Higher than normal electricity bills — system working harder for same output

| 📷 PHOTOS TO TAKE - Condenser coil exterior — full shot and close-up of fin blockage (cottonwood, debris) - Condenser coil interior — shoot through fan grill if accessible - Evaporator coil surface — pull filter and photograph coil face through return plenum - Return grille and filter together — to confirm filter is not also the issue | 📊 READINGS / MEASUREMENTS - Discharge pressure (unit ON): R-410A normal 250–350 PSI. Above 380 PSI with outdoor temp under 95°F → condenser coil blocked - Delta T across indoor coil: should be 18–22°F. Low delta T with normal suction pressure → evaporator coil restricted - Condenser fan amp draw: rises when coil is blocked (motor working harder) - Suction pressure: slightly elevated if condenser coil severely blocked (high head pressure backs up the system) - Water spray test: spray condenser coil with water while gauges connected. If discharge pressure drops >20 PSI in 60 seconds → coil was the restriction |
| --- | --- |

📱 HOW THE APP HANDLES THIS Step 1: App complaint: 'Not cooling well' or 'Running constantly' → app routes to coil check BEFORE refrigerant diagnosis. Step 2: App prompts: 'Is the filter clean?' Yes → 'Now check condenser coil. Is it visibly clogged?' Photograph required. Step 3: App prompts the water spray test: 'With gauges connected, spray coil with water. Record discharge pressure before and after.' App calculates drop. Step 4: If discharge pressure drops >20 PSI → app flags: CONDENSER COIL BLOCKED — clean before any refrigerant work. Step 5: App prompts evaporator coil photo through return plenum. AI detects fin blockage from image. Step 6: Estimate generated: coil cleaning service. Condenser and evaporator are separate line items.

| ✅ OPTION A — GOOD - Brush or blow out condenser coil fins from inside outward with compressed air - Rinse with garden hose from inside out (never outside in — pushes debris deeper) - Replace air filter | 🔧 OPTION B — BETTER - Professional coil cleaning — condenser coil with Nu-Brite or equivalent coil cleaner - Evaporator coil cleaning with no-rinse evaporator cleaner - Clean drain pan and drain line (coil cleaning dislodges algae) - Replace filter | ⭐ OPTION C — BEST - Full coil cleaning — condenser and evaporator - Install coil guard screen on condenser to prevent future cottonwood/debris entry - 4-inch media filter on return for evaporator protection - Annual cleaning contract — flag in app as recurring maintenance item |
| --- | --- | --- |

🔔 LIFECYCLE / PREVENTION Houston cottonwood season (April–May) and summer storms deposit heavy debris on condenser coils. A fully blocked condenser coil presents identically to a refrigerant overcharge on the gauges — high discharge pressure, normal suction. Always do the water spray test before adding refrigerant. App should route dirty coil check BEFORE any refrigerant diagnosis for any 'not cooling' complaint. Annual spring coil cleaning should be a standard line item in every maintenance contract.

| 15. Fixed Orifice / Piston Metering Device (Non-TXV Systems) | HIGH |
| --- | --- |

🔍 SYMPTOMS / WHAT TECH SEES - Not cooling despite compressor running normally - Suction pressure consistently low or high — but without the hunting/cycling signature of a TXV fault - Superheat consistently very high (>20°F) — wrong orifice size for tonnage or worn piston - Superheat consistently very low (<5°F) — oversized orifice or partially blocked piston allowing too much flow - System was recently serviced or recharged and now does not cool correctly (wrong orifice size installed) - Builder-grade unit: Lennox, Carrier, Goodman or Rheem 2005–2015 vintage — most likely fixed orifice

| 📷 PHOTOS TO TAKE - Metering device access panel — photograph the piston/orifice in the liquid line - Serial number plate — to confirm system type (TXV vs fixed orifice) from manufacturer data - Liquid line and suction line at the indoor coil connection — check for oily staining or ice | 📊 READINGS / MEASUREMENTS - Suction pressure (unit ON): compare to refrigerant target. Stable but out of range = orifice issue (not hunting like TXV) - Superheat: HIGH (>20°F consistently) = orifice too small or partially blocked. LOW (<5°F consistently) = orifice too large. - Sub-cooling at liquid line: if sub-cooling is correct but superheat is wrong → metering device is the issue, not refrigerant charge - Pressure drop across liquid line at metering device: check manufacturer spec for normal drop - Orifice physical inspection: remove and measure bore diameter. Compare to manufacturer chart for unit tonnage. |
| --- | --- |

📱 HOW THE APP HANDLES THIS Step 1: App Step 1 prompts: 'Is this system TXV or fixed orifice/piston?' Tech selects. App routes to appropriate diagnostic card. Step 2: App identifies system type from serial number decoder where data available — flags if uncertain and asks tech to confirm. Step 3: For fixed orifice: app prompts superheat reading only (no subcooling hunting check needed). Step 4: App calculates: is superheat stable but wrong? If consistently >20°F → orifice too small or blocked. If <5°F → orifice too large. Step 5: App prompts physical inspection: 'Remove orifice and photograph. Note bore size.' Step 6: App generates estimate: orifice replacement with correct size per tonnage. Includes filter drier replacement.

| ✅ OPTION A — GOOD - Replace orifice/piston with correct size for unit tonnage (check manufacturer chart) - Replace filter drier after any orifice work - Recharge system to nameplate weight + verify superheat | 🔧 OPTION B — BETTER - Replace orifice with correct size - Replace filter drier and liquid line filter - Flush liquid line if contamination suspected - Recharge by weight and verify superheat at multiple ambient temperatures | ⭐ OPTION C — BEST - Replace orifice, filter drier, and liquid line filter - Consider upgrading to TXV kit if manufacturer offers one for the model — TXV outperforms fixed orifice in variable load conditions - Recharge precisely by weight - Full system test — verify superheat at 75°F ambient and 95°F ambient to confirm correct orifice sizing |
| --- | --- | --- |

🔔 LIFECYCLE / PREVENTION Fixed orifice systems are commonly misdiagnosed as TXV failures or refrigerant issues by techs who are not familiar with the platform. A wrong-size orifice installed during a previous service call is a frequent root cause of repeated 'not cooling' callbacks on builder-grade units. App must ask at complaint intake whether system is TXV or fixed orifice and must never apply TXV diagnostic logic to a piston system. The hunting/cycling pressure signature that indicates TXV failure does NOT occur in piston systems.

| 16. Loose Terminal / Wiring Connection Fault | CRITICAL |
| --- | --- |

🔍 SYMPTOMS / WHAT TECH SEES - Unit fails intermittently — works fine then shuts off for no apparent reason - Failure occurs more often after unit has been running 20+ minutes (heat soak causes loose terminal to arc) - Compressor capacitor blew — but a new capacitor keeps failing (root cause is arcing terminal overheating the capacitor) - Burnt smell from outdoor unit disconnect box or contactor area - Breaker trips but resets easily and unit runs again — then trips again later - Wire insulation discoloured, brittle, or melted near terminal block

| 📷 PHOTOS TO TAKE - All compressor terminals — look for discolouration, black carbon, or corrosion - Contactor contact wires — look for burnt wire ends or melted insulation - Outdoor disconnect box interior — check for arcing marks on fuse holders or lugs - Indoor unit terminal board — look for burnt connections, especially on communication wires - Any wire nut connections in line-voltage wiring — these are failure points in Houston humidity | 📊 READINGS / MEASUREMENTS - Voltage at compressor terminals under load: voltage drop >5V between disconnect and compressor terminals = resistance in wiring (loose connection) - Amp draw on each leg (L1 and L2): significant imbalance between legs suggests one has a high-resistance connection - Terminal temperature with infrared thermometer (Phase 2 feature): any terminal running >20°F above ambient while unit runs = loose connection generating heat - Torque check: all terminals should be torqued to nameplate spec (typically 35–45 in-lbs for compressor terminals) - Wire insulation resistance megohm test: any reading below 1 MΩ from conductor to ground = compromised insulation |
| --- | --- |

📱 HOW THE APP HANDLES THIS Step 1: App complaint intake: 'Intermittent shutdown' or 'Breaker trips' → app immediately routes to wiring inspection BEFORE component diagnosis. Step 2: App prompts: 'Inspect all high-voltage terminals with unit powered off. Look for discolouration, corrosion, or melted insulation. Photograph any found.' Step 3: App prompts voltage drop check: 'Measure voltage at disconnect and at compressor terminals simultaneously. Enter both readings.' App calculates drop — if >3V, flags wiring fault. Step 4: App prompts amp draw on L1 and L2. If imbalance >10%, flags possible connection fault on the higher-reading leg. Step 5: If terminal damage is found: app generates estimate for wiring repair and terminal replacement BEFORE any other component work. Step 6: App notes: 'Do not replace capacitor or contactor until terminal fault is repaired — arcing will destroy the new component.'

| ✅ OPTION A — GOOD - Tighten all loose terminals to spec with torque screwdriver - Clean corroded terminals with electrical contact cleaner - Replace any burnt or damaged wire sections with correct gauge wire | 🔧 OPTION B — BETTER - Tighten all terminals to spec - Replace burnt wire sections - Replace any corroded terminal blocks - Install anti-oxidation compound (NoAlox) on all aluminium wire connections - Retest voltage drop and amp imbalance after repair | ⭐ OPTION C — BEST - Full terminal inspection and re-torque on all components - Replace damaged terminal blocks, contactors, and wire runs - Install surge protector on the system (protects against voltage spikes that cause arcing) - Replace any wire nut connections in outdoor wiring with compression connectors - Thermal camera inspection after repair to confirm no remaining hot spots (Phase 2 app feature) |
| --- | --- | --- |

🔔 LIFECYCLE / PREVENTION A loose terminal is the silent root cause behind a long list of misdiagnosed 'component failures.' If a capacitor has blown, always check the terminals before replacing it — a loose compressor terminal will overheat and destroy a new capacitor within a season. In Houston's humidity, aluminium wiring connections (common in older homes) corrode rapidly and are a fire risk if not treated with anti-oxidation compound. App must route all intermittent fault complaints to terminal inspection first. Thermal camera integration (Phase 2) will allow the app to confirm loose terminals from the photo before any wiring is touched.

| 17. Refrigerant Overcharge | HIGH |
| --- | --- |

🔍 SYMPTOMS / WHAT TECH SEES - Both suction AND discharge pressure abnormally high simultaneously - Unit cools weakly despite compressor running at full load - Sub-cooling very high (>20°F) — liquid line backed up with excess refrigerant - Suction line may be sweating excessively or unusually cold - System was recently serviced — previous tech added refrigerant without recovering first - Compressor may trip on high-pressure safety cutout

| 📷 PHOTOS TO TAKE - Gauge manifold showing both suction and discharge simultaneously — photograph while running - Liquid line at service valve — look for excessive sweating or frost - Compressor area — listen for laboured running sound - Previous service records if available — look for 'topped off' entries | 📊 READINGS / MEASUREMENTS - Suction pressure: above normal operating range AND discharge pressure: also above normal — BOTH high simultaneously is the overcharge signature - Sub-cooling at liquid line: above 18°F = overcharged (too much liquid refrigerant in the system) - Compression ratio: will be near-normal or slightly elevated — distinguishes overcharge from compressor failure (which shows LOW ratio) - Delta T: lower than expected despite high pressures — system working harder but transferring less heat - Compare to dirty coil: dirty condenser coil shows HIGH discharge, NORMAL suction. Overcharge shows HIGH discharge AND HIGH suction. |
| --- | --- |

📱 HOW THE APP HANDLES THIS Step 1: App complaint: 'Not cooling well' — after dirty coil ruled out (Branch H), app routes to pressure pattern analysis. Step 2: App prompts: enter suction PSI and discharge PSI with unit running. If both above normal for refrigerant type → app flags: POSSIBLE OVERCHARGE. Step 3: App prompts sub-cooling entry. If sub-cooling >18°F with both pressures high → OVERCHARGE CONFIRMED. Step 4: App asks: 'Was refrigerant added to this system in the last 12 months?' Yes → confirms likely overcharge from improper top-off. Step 5: App generates estimate: refrigerant recovery to nameplate weight + system retest. App flags: do NOT add more refrigerant. Step 6: App notes in the record: system was overcharged. Flags for tech accountability and prevents repeat top-off at next call.

| ✅ OPTION A — GOOD - Recover excess refrigerant until system reaches correct operating pressures and subcooling - Verify suction and discharge normalize after recovery - Retest delta T — should recover to 18–22°F | 🔧 OPTION B — BETTER - Recover to empty, reweigh, recharge to nameplate weight exactly - Verify superheat and subcooling at spec after recharge - Check filter drier — overcharge often accompanies moisture contamination from improper service | ⭐ OPTION C — BEST - Recover fully, replace filter drier (overcharge events stress the drier) - Recharge precisely to nameplate weight - Verify superheat and subcooling at two ambient temperatures (75°F and 95°F) - Document correct charge weight in app record to prevent future overcharge at this unit |
| --- | --- | --- |

🔔 LIFECYCLE / PREVENTION Overcharge is 100% caused by improper service — a previous tech added refrigerant without recovering first, or added the wrong amount. In Houston, this is common because many techs 'top off by feel' using gauge pressures instead of weighing the charge. The diagnostic key: dirty condenser coil = HIGH discharge only. Overcharge = HIGH discharge AND HIGH suction simultaneously. App must distinguish these two before any refrigerant work. Never add refrigerant to a system showing both pressures high.

| 18. System Undersizing / Wrong Tonnage for the Space | MEDIUM |
| --- | --- |

🔍 SYMPTOMS / WHAT TECH SEES - Unit runs continuously — never cycles off — during peak summer hours (95°F+ outdoor temp) - House never reaches setpoint temperature despite all equipment checking out correctly - All 18 other issue cards have been checked and cleared — equipment is healthy - Unit is original installation in a home that has been extended or converted (garage, attic, sunroom added) - Complaints specifically worsen in newly added rooms or additions - Unusually high electric bills for the square footage despite normal equipment health - Realtor or homeowner reports the unit 'has always struggled' since installation

| 📷 PHOTOS TO TAKE - Serial number — photograph for tonnage confirmation (check manufacturer chart for model tonnage) - Electrical panel label — note breaker size for the AC circuit (confirms installed tonnage) - Home floor plan or rough room count — to flag if square footage clearly mismatches equipment size - Any visible room additions, garage conversions, or sunrooms — photograph for documentation | 📊 READINGS / MEASUREMENTS - Unit tonnage from serial number: confirm what is installed. Rule of thumb: 1 ton per 400–600 sq ft in Houston (higher with poor insulation or no attic radiant barrier) - Delta T across air handler: if 18–22°F and refrigerant charge is correct, the equipment is doing its job — the load exceeds capacity - Runtime fraction: if unit runs more than 85% of the time on a 95°F day and cannot hit setpoint, undersizing is confirmed - Electric bill comparison: pull from homeowner — unusually high relative to square footage and similar homes - Manual J load calculation: required for definitive sizing assessment — accounts for insulation R-value, window area, orientation, occupancy, duct efficiency |
| --- | --- |

📱 HOW THE APP HANDLES THIS Step 1: App routes here only after all other 18 cards are cleared — it is the diagnosis of elimination. Step 2: App prompts: 'Has any room been added to this home since original installation?' Yes → flags undersizing risk. Step 3: App calculates rough adequacy: tech enters home square footage and number of bedrooms. App compares to installed tonnage. If below 1 ton per 600 sq ft in Houston → flags: POSSIBLE UNDERSIZING. Step 4: App generates: 'All equipment checks passed. Cooling shortfall may be a system sizing issue. Recommend Manual J load calculation before replacing equipment.' Step 5: App estimate: Manual J assessment as a billable service ($150–300). New system sizing recommendation with replacement quote as Option C. Step 6: App note to tech: never quote a replacement system without a Manual J. Installing another undersized unit is a repeat callback waiting to happen.

| ✅ OPTION A — GOOD - Confirm current tonnage from serial number - Estimate rough load vs installed capacity - Advise homeowner that equipment may be undersized — present as a billable assessment | 🔧 OPTION B — BETTER - Commission a Manual J load calculation ($150–300 billable service) - Identify specific areas of heat gain (attic insulation, window exposure, duct losses) - Quote appropriately sized replacement system with correct tonnage | ⭐ OPTION C — BEST - Full Manual J load calculation - Identify and address heat gain sources first: attic radiant barrier, window film, duct sealing — these reduce required tonnage - Quote correctly sized system - Include energy modelling: show homeowner 5-year operating cost difference between undersized current unit running constantly vs correctly sized new unit |
| --- | --- | --- |

🔔 LIFECYCLE / PREVENTION Undersizing is the diagnosis of elimination — you only arrive here after every other card clears. The mistake techs make is quoting a like-for-like replacement without checking if the original unit was correctly sized. Houston homes with additions, high-gain windows, or poor attic insulation regularly need more tonnage than the original builder spec. Never quote a replacement system by matching the existing unit size — always do a Manual J or you are installing the same problem again.

| 19. Formicary Corrosion on Evaporator Coil (Pinhole Leak) | HIGH |
| --- | --- |

🔍 SYMPTOMS / WHAT TECH SEES - Slow, gradual loss of refrigerant charge over months — system needs top-off repeatedly - No visible oily residue at pipe joints or flare fittings — no obvious leak point - Electronic leak detector triggers at the evaporator coil face but no visible damage - New construction or recently renovated home — off-gassing from building materials is the cause - Homes with heavy use of cleaning products containing formic acid (certain wood floor cleaners, ant killers) - Leak is at the coil itself, not at any joint or fitting — this is the diagnostic key - Previous techs have recharged the system multiple times without finding the leak

| 📷 PHOTOS TO TAKE - Evaporator coil face — photograph through return plenum with good lighting (look for green or white powder deposits on copper fins — this is the corrosion signature) - Any green or turquoise discolouration on copper tubing at or near the coil - Indoor air handler access panel — look for oily residue on the coil drain pan (refrigerant oil from pinhole leak collects here) - Electronic leak detector probe path — photograph the position where detector alarmed | 📊 READINGS / MEASUREMENTS - Electronic leak detector: sweep slowly across the coil face in a grid pattern. Any alarm at the coil face with no alarm at fittings = formicary corrosion leak - Refrigerant standing pressure: compare to prior service records if available — gradual drop over months confirms slow leak - Fluorescent dye inspection: if dye was added at prior service, UV lamp will show leak location on coil face - Visual: green or white powder on copper fins is formic acid corrosion product — this is definitive visual confirmation even before detector - Superheat: elevated superheat with clean filter and correct airflow = low charge = leak somewhere |
| --- | --- |

📱 HOW THE APP HANDLES THIS Step 1: App complaint: 'System was recharged 6 months ago and is not cooling again.' This pattern immediately flags formicary corrosion or slow leak. Step 2: App prompts: 'Has the system required recharging more than once in 24 months?' Yes → app flags: REPEAT LEAK — check coil face for formicary corrosion before checking fittings. Step 3: App prompts leak detector sweep of coil face. Tech enters result. If alarm at coil, no alarm at fittings → app flags: FORMICARY CORROSION SUSPECTED. Step 4: App prompts photo of coil face. AI looks for green/turquoise powder on fins. Step 5: App generates estimate: coil replacement (formicary corrosion cannot be patched — once pinholes form the entire coil must be replaced). Step 6: App flags: identify and remove the acid source (cleaning products, building materials off-gassing) or corrosion will recur on the new coil.

| ✅ OPTION A — GOOD - Locate the leak with electronic detector and UV dye - Document leak position on coil for warranty claim if unit is under warranty - Advise homeowner that pinhole corrosion cannot be repaired — coil replacement required | 🔧 OPTION B — BETTER - Replace evaporator coil - Replace filter drier after coil work - Recharge to nameplate weight - Advise homeowner to remove formic acid sources from the home — identify and discontinue the causative cleaning products | ⭐ OPTION C — BEST - Replace evaporator coil with upgraded coil — consider Carrier WeatherArmor or Lennox XC coil with corrosion-resistant coating if home has ongoing acid source - Replace filter drier - Test air quality for VOC levels if new construction — this is a builder defect issue that may be a warranty claim against the builder - Recharge precisely, verify leak-free at 30 days |
| --- | --- | --- |

🔔 LIFECYCLE / PREVENTION Formicary corrosion is caused by copper reacting with formic acid in the indoor air — from certain wood floor finishes, particle board off-gassing (formaldehyde → formic acid), ant poison, or cleaning products. It produces microscopic pinholes that are invisible to the naked eye. The diagnostic signature is: slow refrigerant loss, no visible leak at any fitting, detector alarms at the coil face, green or white powder on the fins. Common in Houston new construction (builder-grade materials off-gas heavily in the first 2–3 years). App should flag this possibility on any system requiring a second recharge within 24 months.

# PART 3 — Quick Reference: Target Readings by Refrigerant Type

App should display this reference whenever the tech is entering pressure readings. Auto-select the table based on refrigerant type identified from the serial number.

## R-410A (2010–2023 systems — most common in Houston)

| Parameter | Normal Range | Below Normal | Above Normal |
| --- | --- | --- | --- |
| Suction Pressure | 115–125 PSI | <100 PSI = low charge or restriction | >135 PSI = high load or overcharge |
| Discharge Pressure | 250–350 PSI (varies with ambient) | <220 PSI = low charge or compressor | 400+ PSI = condenser blockage or overcharge |
| Superheat (TXV systems) | 8–14°F | >18°F = undercharged or TXV closed | <5°F = overcharged or TXV open |
| Sub-cooling | 10–15°F | <8°F = undercharged | >18°F = overcharged or liquid line restriction |
| Delta T (supply vs return) | 18–22°F | <14°F = airflow or refrigerant problem | >25°F = possible TXV restriction |

## R-22 (Pre-2010 systems — LEGACY, phase-out pricing applies)

R-22 PRICING ALERT R-22 is no longer manufactured. Current price: $80–120/lb vs $12–18/lb for R-410A. For any R-22 leak, Option C must always be full system replacement. App must flag this automatically from serial number decode.

| Parameter | Normal Range | Below Normal | Above Normal |
| --- | --- | --- | --- |
| Suction Pressure | 60–75 PSI | <55 PSI = low charge | >85 PSI = overcharge or high load |
| Discharge Pressure | 200–275 PSI | <180 PSI = low charge or compressor | >300 PSI = condenser problem |
| Superheat | 10–20°F | >25°F = undercharged | <5°F = overcharged |
| Sub-cooling | 10–18°F | <8°F = undercharged | >20°F = overcharged |

## Electrical Reference — All Systems

| Measurement | Acceptable | Investigate | Failed |
| --- | --- | --- | --- |
| Supply voltage | 215–245V | <215V or >250V = call electrician | <200V = unit damage risk |
| Capacitor reading | Within ±6% of nameplate MFD | 6–15% below nameplate = weakening | >15% below nameplate = replace now |
| Compressor amp draw | At or below nameplate RLA | 101–115% of RLA = monitor | Over 115% of RLA = compressor failing |
| 24V control circuit | 22–28V | <20V = transformer or wiring issue | <15V = system will not operate reliably |
| Contactor coil resistance | 8–20Ω | OL (open) = coil failed | 0Ω = shorted coil |

# PART 4 — SnapAI App Workflow: End-to-End for Every Job

This is the complete sequence the app should walk a technician through on every service call, from the moment they open the app to the moment the estimate is sent to the homeowner.

## Step 1 — Property & Equipment Identification (30 seconds)

- Tech opens app, selects property or creates new one. Address auto-fills from previous visits.

- Tech photographs the nameplate/serial number. App decodes automatically: brand, model, tonnage, age, refrigerant type, warranty status.

- App flags immediately: R-22 system? Equipment over 12 years? Compressor in warning window?

## Step 2 — Complaint Intake (1 minute)

- App presents: 'What is the customer complaining about?' — short list of complaint types.

- Tech selects one or more complaints. This selection drives all subsequent prompts.

- App enters the correct branch of the decision tree based on complaint.

## Step 3 — Mandatory Readings (cooling complaints: required gate)

- For cooling complaints: app hard-gates at this step. Tech cannot proceed without entering suction PSI, discharge PSI, supply temp, and return temp.

- App shows target ranges for the detected refrigerant type (R-22, R-410A, or R-32).

- If suction line temperature is entered, app calculates superheat automatically.

- If liquid line temperature is entered, app calculates sub-cooling automatically.

- App flags any readings outside normal range with colour-coded alerts.

## Step 4 — Issue-Specific Photo Capture

- Based on complaint and readings, app tells the tech exactly which 3 photos to take.

- Each photo prompt includes a diagram showing what part to frame and from what angle.

- Tech takes photos. AI runs YOLO detection and XGBoost sensor analysis simultaneously.

- If AI confidence is below threshold, Gemini tiebreaker is called with full context loaded.

## Step 5 — Diagnosis Confirmation

- App presents confirmed diagnosis: fault label, confidence percentage, supporting evidence.

- Tech can accept or override. Override is recorded for model retraining.

- App shows: 'This diagnosis is consistent with: [list of matching readings and visual evidence].'

## Step 6 — Estimate Generation

- App generates Good / Better / Best options based on diagnosed fault + unit age + refrigerant type.

- Parts pricing pulled from brand/model database (Phase 2). Labour hours from job type matrix.

- Recommended badge applied based on unit age and condition — not hardcoded.

- R-22 alert: if R-22 system with any leak, Option C is always full replacement. App enforces this.

- Homeowner narrative generated: plain English explanation of what is wrong and why.

## Step 7 — Review, Send, and Follow-up

- Tech reviews estimate on PDF preview. Can adjust any line item.

- If adjusted, app records the correction (feedback loop for AI improvement).

- Tech sends to homeowner via email. Homeowner report link generated.

- App automatically schedules: 24h, 48h, and 7-day follow-up emails.

- Lifecycle reminders created for this unit: component age flags based on install date.

Mark's Final Word If this app does all seven steps correctly, it turns a junior tech into someone who works like a 10-year veteran. They will not miss the capacitor. They will not quote a compressor when the filter was the problem. They will not recharge R-22 when the homeowner needs a new system. That is the real value here — not just the estimate, but the diagnosis that justifies it.