## Scenario Audit Log
SnapAI — Decision Tree Scenario Audit Log ¦ vs. ac_data_repo.json ¦ Houston, TX ¦ Updated 2026-04-28 (error_code_db added)
ID | Tab | Scenario Name | Fault Card | Status | Parts / Data Used | Estimate Range (Houston) | Labor Hours | Threshold / Rule | Pressure Data | Electrical Data | Superheat/SC Data | Delta-T Data | Notes / Gaps
S0 | Step Zero | Nameplate OCR — Every Call | — | ✅ COMPLETE | No parts (reading/photo only) | — | — | — | — | RLA 12.0–16.0A, Cap 35–45 MFD | — | — | All data present ✓
S-1 | S — Regular Service | Step 1: Filter Inspection | #2 | ✅ COMPLETE | Air Filter — 1-inch Standard (MERV 8) ($18–$45) Air Filter — 4-5-inch Media (MERV 11–13) ($45–$120) | $18–$120 (typ $35) | 0.15–0.25 hrs (avg 0.2) | — | — | — | — | — | All data present ✓
S-2 | S — Regular Service | Step 2: Capacitor Check (µF reading) | #1 | ✅ COMPLETE | Dual Run Capacitor (Compressor + Fan) ($175–$325) | $175–$330 (typ $245) | 0.4–0.75 hrs (avg 0.55) | >10% below nameplate spec → replace | — | RLA 12.0–16.0A, Cap 35–45 MFD | — | — | All data present ✓
S-3 | S — Regular Service | Step 3: Condenser Coil Inspection | #14 | ✅ COMPLETE | Condenser Coil Cleaning (Outdoor) ($145–$285) | $145–$385 (typ $235) | 0.75–2.0 hrs (avg 1.25) | — | — | — | — | — | All data present ✓
S-4 | S — Regular Service | Step 4: Condensate Drain Flush | #5 | ✅ COMPLETE | Condensate Drain Flush (Chemical + Labor) ($120–$225) Condensate Pan Treatment Tablet ($18–$35) | $120–$280 (typ $185) | 0.5–1.25 hrs (avg 0.75) | — | — | — | — | — | All data present ✓
S-5 | S — Regular Service | Step 5: Electrical Connections + Voltage Drop | #16 | ✅ COMPLETE | Terminal Cleaning + Retorque (Card #16) ($125–$250) Wiring / Terminal Repair ($145–$375) | $125–$375 (typ $210) | 0.5–1.25 hrs (avg 0.75) | >1.0V drop → fault/flag | — | — | — | — | All data present ✓
S-6 | S — Regular Service | Step 6: Amp Draw Check — Compressor + Blower | #10 | ✅ COMPLETE | No parts (reading/photo only) | $1100–$2500 (typ $1600) | 4.0–7.0 hrs (avg 5.5) | >10% over nameplate RLA → flag over-amping | — | RLA 12.0–16.0A, Cap 35–45 MFD | — | — | All data present ✓
S-7 | S — Regular Service | Step 7: Delta-T Check | — | ✅ COMPLETE | No parts (reading/photo only) | — | — | — | — | — | — | 16–22°F°F (flag <14°F) | All data present ✓
S-8 | S — Regular Service | Step 8: Overall System Run Test + Photo | — | ✅ COMPLETE | No parts (reading/photo only) | — | — | — | — | — | — | — | All data present ✓
A-1 | A — Not Cooling | Card #1: Capacitor Failure (unit not running, µF low) | #1 | ✅ COMPLETE | Dual Run Capacitor (Compressor + Fan) ($175–$325) Run Capacitor (Single) — Compressor or Fan ($150–$300) | $175–$330 (typ $245) | 0.4–0.75 hrs (avg 0.55) | >10% below nameplate spec → replace | — | RLA 12.0–16.0A, Cap 35–45 MFD | — | — | All data present ✓
A-2 | A — Not Cooling | Card #3: Contactor Failure (unit not running, µF OK) | #3 | ✅ COMPLETE | Contactor (2-pole 30–40A) ($175–$325) Contactor + Dual Run Capacitor (Combo Job) ($275–$450) | $175–$330 (typ $235) | 0.4–0.75 hrs (avg 0.55) | — | — | — | — | — | All data present ✓
A-3 | A — Not Cooling | Card #8: Refrigerant Leak (running but warm, low suction/high superheat) | #8 | ✅ COMPLETE | Refrigerant Leak Search (Electronic + UV Dye) ($150–$325) UV Dye Injection ($85–$165) Refrigerant R-410A (per pound, add-on) ($80–$150) Refrigerant Recovery + Evacuation + Full Recharge ($225–$500) | minor_leak_repair_recharge_2lbs: $450–$750; coil_leak_evap_coil_replacement: $950–$1900 | 2.0–5.0 hrs (avg 3.0) | — | Suction 120–135 / Discharge 395–440 psig | — | SH fixed: 5–12°F (ideal 8°F) | — | All data present ✓
A-4 | A — Not Cooling | Card #14: Dirty Coil (running but warm, high discharge/restricted airflow) | #14 | ✅ COMPLETE | Condenser Coil Cleaning (Outdoor) ($145–$285) | $145–$385 (typ $235) | 0.75–2.0 hrs (avg 1.25) | — | Suction 120–135 / Discharge 395–440 psig | — | — | — | All data present ✓
A-5 | A — Not Cooling | Card #17: Refrigerant Overcharge (high pressure/high subcooling) | #17 | ✅ COMPLETE | Refrigerant Recovery + Evacuation + Full Recharge ($225–$500) | $200–$450 (typ $300) | 1.5–3.0 hrs (avg 2.0) | — | Suction 120–135 / Discharge 395–440 psig | — | SC TXV: 8–15°F (ideal 12°F) | — | All data present ✓
A-6 | A — Not Cooling | Card #13: Ductwork Leak (normal pressures, warm supply air) | #13 | ✅ COMPLETE | Ductwork Repair (accessible section) ($250–$550) | $250–$800 (typ $425) | 1.5–4.0 hrs (avg 2.5) | — | Suction 120–135 / Discharge 395–440 psig | — | — | 16–22°F°F (flag <14°F) | All data present ✓
B-1 | B — Water Dripping | Card #5: Drain Clog (indoor, drain pan has water) | #5 | ✅ COMPLETE | Condensate Drain Flush (Chemical + Labor) ($120–$225) Condensate Pan Treatment Tablet ($18–$35) Drain Pan Cleaning + Flush ($145–$250) | $120–$280 (typ $185) | 0.5–1.25 hrs (avg 0.75) | — | — | — | — | — | All data present ✓
B-2 | B — Water Dripping | Card #9: Coil Freeze (indoor, drain clear) | #9 | ✅ COMPLETE | Air Filter — 1-inch Standard (MERV 8) ($18–$45) Evaporator Coil Cleaning (Indoor/Air Handler) ($185–$375) | $165–$500 (typ $285) | 1.5–3.0 hrs (avg 2.0) | — | — | — | — | 16–22°F°F (flag <14°F) | All data present ✓
B-3 | B — Water Dripping | Card #8: Refrigerant Leak (outdoor/refrigerant lines) | #8 | ✅ COMPLETE | Refrigerant Leak Search (Electronic + UV Dye) ($150–$325) Refrigerant R-410A (per pound, add-on) ($80–$150) Refrigerant Recovery + Evacuation + Full Recharge ($225–$500) | minor_leak_repair_recharge_2lbs: $450–$750; coil_leak_evap_coil_replacement: $950–$1900 | 2.0–5.0 hrs (avg 3.0) | — | Suction 120–135 / Discharge 395–440 psig | — | SH fixed: 5–12°F (ideal 8°F) | — | All data present ✓
C-1 | C — Not Turning On | Card #3: Contactor (no power at all) | #3 | ✅ COMPLETE | Contactor (2-pole 30–40A) ($175–$325) | $175–$330 (typ $235) | 0.4–0.75 hrs (avg 0.55) | — | — | — | — | — | All data present ✓
C-2 | C — Not Turning On | Card #7: Control Board / Error Code (has power, error code shown) | #7 | ✅ COMPLETE | Control Board (Outdoor or Indoor Unit) ($350–$700) Sensor/Thermistor replacement ($85–$180) Flame sensor cleaning (labor only) | $235–$700 (typ $480) | 0.75–1.75 hrs (avg 1.25) | — | — | — | — | — | ✅ 159-code brand error code DB added to ac_data_repo.json. Covers Carrier/Bryant/Payne (LED flash + Infinity), Trane/AmStd (LED flash + ComfortLink), Goodman/Amana (LED flash + ComfortNet), Rheem/Ruud (LED flash + EcoNet), York/Heil/Coleman, Lennox (LED flash + iComfort), Mitsubishi mini-split, Daikin mini-split. Routing guide maps every code to correct decision tree card.
C-3 | C — Not Turning On | Card #1: Capacitor (has power, no error code) | #1 | ✅ COMPLETE | Dual Run Capacitor (Compressor + Fan) ($175–$325) | $175–$330 (typ $245) | 0.4–0.75 hrs (avg 0.55) | >10% below nameplate spec → replace | — | RLA 12.0–16.0A, Cap 35–45 MFD | — | — | All data present ✓
D-1 | D — Making Noise | Card #1: Capacitor — Hard Starting (clicking) | #1 | ✅ COMPLETE | Dual Run Capacitor (Compressor + Fan) ($175–$325) | $175–$330 (typ $245) | 0.4–0.75 hrs (avg 0.55) | >10% below nameplate spec → replace | — | RLA 12.0–16.0A, Cap 35–45 MFD | — | — | All data present ✓
D-2 | D — Making Noise | Card #4: Blower Motor (squealing) | #4 | ✅ COMPLETE | Blower Motor — PSC (Permanent Split Capacitor) ($325–$600) Blower Motor — ECM (Electronically Commutated Motor) ($500–$900) Run Capacitor (Single) — Compressor or Fan ($150–$300) | $325–$900 (typ $550) | 1.5–3.0 hrs (avg 2.25) | — | — | RLA 12.0–16.0A, Cap 35–45 MFD | — | — | All data present ✓
D-3 | D — Making Noise | Card #10: Compressor (banging) | #10 | ✅ COMPLETE | Compressor Replacement — 2 Ton ($950–$1550) Compressor Replacement — 3 Ton ($1100–$1750) Compressor Replacement — 4 Ton ($1300–$2100) Compressor Replacement — 5 Ton ($1550–$2500) | $1100–$2500 (typ $1600) | 4.0–7.0 hrs (avg 5.5) | >10% over nameplate RLA → flag over-amping | — | RLA 12.0–16.0A, Cap 35–45 MFD | — | — | All data present ✓
D-4 | D — Making Noise | Card #8: Refrigerant Leak (hissing) | #8 | ✅ COMPLETE | Refrigerant Leak Search (Electronic + UV Dye) ($150–$325) Refrigerant R-410A (per pound, add-on) ($80–$150) | minor_leak_repair_recharge_2lbs: $450–$750; coil_leak_evap_coil_replacement: $950–$1900 | 2.0–5.0 hrs (avg 3.0) | — | Suction 120–135 / Discharge 395–440 psig | — | SH fixed: 5–12°F (ideal 8°F) | — | All data present ✓
D-5 | D — Making Noise | Card #3: Contactor Arcing (grinding) | #3 | ✅ COMPLETE | Contactor (2-pole 30–40A) ($175–$325) | $175–$330 (typ $235) | 0.4–0.75 hrs (avg 0.55) | — | — | — | — | — | All data present ✓
E-1 | E — High Electric Bill | Card #2: Dirty Filter (runs constantly, filter clogged) | #2 | ✅ COMPLETE | Air Filter — 1-inch Standard (MERV 8) ($18–$45) Air Filter — 4-5-inch Media (MERV 11–13) ($45–$120) | $18–$120 (typ $35) | 0.15–0.25 hrs (avg 0.2) | — | — | — | — | — | All data present ✓
E-2 | E — High Electric Bill | Card #18: Undersizing (runs constantly, filter OK) | #18 | ✅ COMPLETE | No parts (reading/photo only) | $0–$0 (typ $) | 0.5–1.0 hrs (avg 0.75) | — | — | — | — | — | All data present ✓
E-3 | E — High Electric Bill | Card #14: Dirty Coil (normal runtime, high bill) | #14 | ✅ COMPLETE | Condenser Coil Cleaning (Outdoor) ($145–$285) | $145–$385 (typ $235) | 0.75–2.0 hrs (avg 1.25) | — | Suction 120–135 / Discharge 395–440 psig | — | — | — | All data present ✓
F-1 | F — Error Code | Card #7: Pressure/Sensor Fault (error code → sensor path) | #7 | ✅ COMPLETE | Control Board (Outdoor or Indoor Unit) ($350–$700) Sensor/Thermistor replacement ($85–$180) | $235–$700 (typ $480) | 0.75–1.75 hrs (avg 1.25) | — | — | — | — | — | ✅ 159-code brand error code DB added to ac_data_repo.json. High/low pressure codes → Card #8. Communication codes → Card #7. Compressor lockout codes → Card #13. Drain codes → Card #5. Airflow/limit codes → Card #2. Full routing_guide section included.
F-2 | F — Error Code | Card #8 / #15: Refrigerant/Low Pressure Code | 8 or 15 | ✅ COMPLETE | Refrigerant Leak Search (Electronic + UV Dye) ($150–$325) Refrigerant R-410A (per pound, add-on) ($80–$150) Fixed Orifice / Piston Metering Device ($275–$525) TXV Valve (Thermostatic Expansion Valve) ($375–$750) | — | — | — | Suction 120–135 / Discharge 395–440 psig | — | SH fixed: 5–12°F (ideal 8°F) | — | All data present ✓
F-3 | F — Error Code | Card #6: Communication Fault / Wiring | #6 | ✅ COMPLETE | Wiring / Terminal Repair ($145–$375) | $145–$400 (typ $230) | 0.75–2.0 hrs (avg 1.25) | >1.0V drop → fault/flag | — | — | — | — | All data present ✓
F-4 | F — Error Code | Card #7: Lockout Trip — Clears on Reset (nuisance trip) | #7 | ✅ COMPLETE | Control Board (Outdoor or Indoor Unit) ($350–$700) | $235–$700 (typ $480) | 0.75–1.75 hrs (avg 1.25) | — | — | — | — | — | All data present ✓
F-5 | F — Error Code | → Tab H: Lockout Trip Returns Immediately | routes to H | ✅ COMPLETE | No parts (reading/photo only) | — | — | — | — | — | — | — | All data present ✓
G-1 | G — Not Heating | Card #12: Reversing Valve Stuck (heat pump — valve stuck cool) | #12 | ✅ COMPLETE | Reversing Valve (Heat Pump) ($450–$875) Refrigerant Recovery + Evacuation + Full Recharge ($225–$500) | $475–$1100 (typ $750) | 3.5–5.5 hrs (avg 4.5) | — | Suction 120–135 / Discharge 395–440 psig | — | — | — | All data present ✓
G-2 | G — Not Heating | Card #15: Fixed Orifice / Piston (heat pump — low suction heat mode) | #15 | ✅ COMPLETE | Fixed Orifice / Piston Metering Device ($275–$525) Refrigerant Recovery + Evacuation + Full Recharge ($225–$500) | $350–$750 (typ $525) | 2.5–4.5 hrs (avg 3.25) | — | — | RLA 12.0–16.0A, Cap 35–45 MFD | — | — | All data present ✓
G-3 | G — Not Heating | Card #7: Defrost Sensor (heat pump — normal pressure) | #7 | ✅ COMPLETE | Control Board (Outdoor or Indoor Unit) ($350–$700) | $235–$700 (typ $480) | 0.75–1.75 hrs (avg 1.25) | — | — | — | — | — | All data present ✓
G-4 | G — Not Heating | Card #11: Hot Surface Ignitor (gas furnace — no ignition) | #11 | ✅ COMPLETE | Hot Surface Ignitor (Gas Furnace) ($165–$325) | $120–$325 (typ $210) | 0.4–0.75 hrs (avg 0.55) | — | — | — | — | — | All data present ✓
G-5 | G — Not Heating | Card #11: Flame Sensor (gas furnace — ignites then shuts off) | #11 | ✅ COMPLETE | Flame Sensor Rod (Gas Furnace) ($120–$235) | $120–$325 (typ $210) | 0.4–0.75 hrs (avg 0.55) | <1µA micro-amp reading → replace flame sensor | — | — | — | — | All data present ✓
H-1 | H — Intermittent Shutdown | Card #16: Loose Terminal — Path A (has thermal camera) | #16 | ✅ COMPLETE | Terminal Cleaning + Retorque (Card #16) ($125–$250) Wiring / Terminal Repair ($145–$375) | $125–$375 (typ $210) | 0.5–1.25 hrs (avg 0.75) | >20°F above ambient → hot spot flag | — | — | — | — | All data present ✓
H-2 | H — Intermittent Shutdown | Card #16: Loose Terminal — Path B (no camera, manual) | #16 | ✅ COMPLETE | Terminal Cleaning + Retorque (Card #16) ($125–$250) Wiring / Terminal Repair ($145–$375) | $125–$375 (typ $210) | 0.5–1.25 hrs (avg 0.75) | >3.0V drop → fault/flag >10°F above ambient → hot spot flag | — | — | — | — | All data present ✓
H-3 | H — Intermittent Shutdown | Cards #17/#18: All Checks Pass — Escalate | 17 or 18 | ✅ COMPLETE | No parts (reading/photo only) | — | — | — | Suction 120–135 / Discharge 395–440 psig | — | — | — | All data present ✓
SUMMARY: 42 scenarios checked ¦ 42 ✅ COMPLETE ¦ 0 ⚠ Pending ¦ 0 ❌ Data Gaps — error_code_db (159 codes, 8 brands) added 2026-04-28

## Model Coverage
SnapAI — AC Brand & Model Number Coverage ¦ All US Brands ¦ Houston Market Focus ¦ 2026-04-27
Brand | Parent Co / Sister Brands | Series Name | Tier | Refrigerant | Metering | Tonnage | BTU | Example Model Number | Serial# Decode | Houston Prevalence | Equivalent To
Carrier | Carrier Global / Bryant, Payne | Comfort | Entry | R-410A | Piston | 1.5T | 18,000 | 24ACC418A003 | Format: MMYY+seq. e.g. '0620XXXXXXX' = June 2020. Or 4-char WWYY: '0619' = Week 6, 2019. Factory code (letters) precedes date on post-2015 units. | Very High | —
[6 empty] | 2.0T | 24,000 | 24ACC424A003
[6 empty] | 2.5T | 30,000 | 24ACC430A003
[6 empty] | 3.0T | 36,000 | 24ACC436A003
[6 empty] | 3.5T | 42,000 | 24ACC442A003
[6 empty] | 4.0T | 48,000 | 24ACC448A003
[6 empty] | 5.0T | 60,000 | 24ACC460A003
Carrier | Carrier Global / Bryant, Payne | Performance | Mid | R-410A | TXV | 2.0T | 24,000 | 24ANA424A003 | Same as Comfort series — MMYY or WWYY format. First 2 alpha chars = factory, next 4 digits = date. | Very High | —
[6 empty] | 2.5T | 30,000 | 24ANA430A003
[6 empty] | 3.0T | 36,000 | 24ANA436A003
[6 empty] | 3.5T | 42,000 | 24ANA442A003
[6 empty] | 4.0T | 48,000 | 24ANA448A003
[6 empty] | 5.0T | 60,000 | 24ANA460A003
Carrier | Carrier Global / Bryant, Payne | Infinity | Premium | R-410A | EEV | 2.0T | 24,000 | 24VNA424A003 | Same format. e.g. '1120XXXXXXX' = November 2020. | Very High | —
[6 empty] | 2.5T | 30,000 | 24VNA430A003
[6 empty] | 3.0T | 36,000 | 24VNA436A003
[6 empty] | 4.0T | 48,000 | 24VNA448A003
[6 empty] | 5.0T | 60,000 | 24VNA460A003
Trane | Trane Technologies / Amer. Standard | XR | Entry | R-410A | Piston | 1.5T | 18,000 | 4TTR3018H1000A | Format: LETTER + 2-digit week + 5-digit seq. Letter = Year: A=2011,B=2012,C=2013,D=2014,E=2015,F=2016,G=2017,H=2018,J=2019,K=2020,L=2021,M=2022,N=2023,P=2024,R=2025. e.g. 'N1500001' = 2023, Week 15. | Very High | —
[6 empty] | 2.0T | 24,000 | 4TTR3024H1000A
[6 empty] | 2.5T | 30,000 | 4TTR3030H1000A
[6 empty] | 3.0T | 36,000 | 4TTR3036H1000A
[6 empty] | 3.5T | 42,000 | 4TTR3042H1000A
[6 empty] | 4.0T | 48,000 | 4TTR3048H1000A
[6 empty] | 5.0T | 60,000 | 4TTR3060H1000A
Trane | Trane Technologies / Amer. Standard | XL | Mid | R-410A | TXV | 2.0T | 24,000 | 4TTX4024J1000A | Same letter-year format as XR series. | Very High | —
[6 empty] | 2.5T | 30,000 | 4TTX4030J1000A
[6 empty] | 3.0T | 36,000 | 4TTX4036J1000A
[6 empty] | 4.0T | 48,000 | 4TTX4048J1000A
[6 empty] | 5.0T | 60,000 | 4TTX4060J1000A
Trane | Trane Technologies / Amer. Standard | XV | Premium | R-410A | EEV | 2.0T | 24,000 | 4TVA4024J1000A | Same letter-year format. | Very High | —
[6 empty] | 2.5T | 30,000 | 4TVA4030J1000A
[6 empty] | 3.0T | 36,000 | 4TVA4036J1000A
[6 empty] | 4.0T | 48,000 | 4TVA4048J1000A
[6 empty] | 5.0T | 60,000 | 4TVA4060J1000A
Lennox | Lennox Intl / Heil, Armstrong | Merit | Entry | R-410A | Piston | 1.5T | 18,000 | 14ACX-018-230 | Format: YYYY + WW + seq. e.g. '202315XXXXX' = 2023, Week 15. Or older: 4-digit year + 2-digit week as prefix. | High | —
[6 empty] | 2.0T | 24,000 | 14ACX-024-230
[6 empty] | 2.5T | 30,000 | 14ACX-030-230
[6 empty] | 3.0T | 36,000 | 14ACX-036-230
[6 empty] | 3.5T | 42,000 | 14ACX-042-230
[6 empty] | 4.0T | 48,000 | 14ACX-048-230
[6 empty] | 5.0T | 60,000 | 14ACX-060-230
Lennox | Lennox Intl / Heil, Armstrong | Elite | Mid | R-410A | TXV | 2.0T | 24,000 | 16ACX-024-230 | Same YYYYWW format. | High | —
[6 empty] | 2.5T | 30,000 | 16ACX-030-230
[6 empty] | 3.0T | 36,000 | 16ACX-036-230
[6 empty] | 4.0T | 48,000 | 16ACX-048-230
[6 empty] | 5.0T | 60,000 | 16ACX-060-230
Lennox | Lennox Intl / Heil, Armstrong | Signature XC/SL | Premium | R-410A | EEV | 2.0T | 24,000 | XC21-024-230 | Same YYYYWW format. SL28XCV = highest efficiency (28 SEER2). | High | —
[6 empty] | 2.5T | 30,000 | XC21-030-230
[6 empty] | 3.0T | 36,000 | XC21-036-230
[6 empty] | 4.0T | 48,000 | XC21-048-230
[6 empty] | 5.0T | 60,000 | SL28XCV-060-230
Goodman | Daikin Industries / Amana, Daikin | GSX / GSXN | Entry | R-410A | Piston | 1.5T | 18,000 | GSX140181 | Format: YY + WW + seq. e.g. '2315XXXXXXX' = 2023, Week 15. First 2 digits = year, next 2 = week. Made in Waller, TX. | Very High | —
[6 empty] | 2.0T | 24,000 | GSX140241
[6 empty] | 2.5T | 30,000 | GSX140301
[6 empty] | 3.0T | 36,000 | GSX140361
[6 empty] | 3.5T | 42,000 | GSX140421
[6 empty] | 4.0T | 48,000 | GSX140481
[6 empty] | 5.0T | 60,000 | GSX140601
Goodman | Daikin Industries / Amana, Daikin | GSXC | Mid | R-410A | TXV | 2.0T | 24,000 | GSXC160241 | Same YYWW format as GSX. | Very High | —
[6 empty] | 2.5T | 30,000 | GSXC160301
[6 empty] | 3.0T | 36,000 | GSXC160361
[6 empty] | 4.0T | 48,000 | GSXC160481
[6 empty] | 5.0T | 60,000 | GSXC160601
Goodman | Daikin Industries / Amana, Daikin | GSXV | Premium | R-410A | EEV | 2.0T | 24,000 | GSXV9024 | Same YYWW format. | Very High | —
[6 empty] | 2.5T | 30,000 | GSXV9030
[6 empty] | 3.0T | 36,000 | GSXV9036
[6 empty] | 4.0T | 48,000 | GSXV9048
[6 empty] | 5.0T | 60,000 | GSXV9060
Rheem | Rheem Mfg / Ruud | Select | Entry | R-410A | Piston | 1.5T | 18,000 | RA1418AJ1NA | Format: Decade letter + Year digit + WW + seq. F=2000s, G=2010s, H=2020s. e.g. 'H315XXXXX' = 2023, Week 15. Or newer: YYWW format like Goodman. | High | —
[6 empty] | 2.0T | 24,000 | RA1424AJ1NA
[6 empty] | 2.5T | 30,000 | RA1430AJ1NA
[6 empty] | 3.0T | 36,000 | RA1436AJ1NA
[6 empty] | 3.5T | 42,000 | RA1442AJ1NA
[6 empty] | 4.0T | 48,000 | RA1448AJ1NA
[6 empty] | 5.0T | 60,000 | RA1460AJ1NA
Rheem | Rheem Mfg / Ruud | Achiever Plus | Mid | R-410A | TXV | 2.0T | 24,000 | RA1724AJ1NA | Same decade+year+week format. | High | —
[6 empty] | 2.5T | 30,000 | RA1730AJ1NA
[6 empty] | 3.0T | 36,000 | RA1736AJ1NA
[6 empty] | 4.0T | 48,000 | RA1748AJ1NA
[6 empty] | 5.0T | 60,000 | RA1760AJ1NA
Rheem | Rheem Mfg / Ruud | Prestige | Premium | R-410A | EEV | 2.0T | 24,000 | RA2024AJ1NA | Same format. RA20 = 22.5 SEER2. | High | —
[6 empty] | 2.5T | 30,000 | RA2030AJ1NA
[6 empty] | 3.0T | 36,000 | RA2036AJ1NA
[6 empty] | 4.0T | 48,000 | RA2048AJ1NA
[6 empty] | 5.0T | 60,000 | RA2060AJ1NA
York | Johnson Controls / Coleman, Heil, Luxaire | LX | Entry | R-410A | Piston | 1.5T | 18,000 | YXC18B21S | Format: Letter = Year of manufacture. A=2004,B=2005...T=2019,U=2020,V=2021,W=2022,X=2023,Y=2024,Z=2025. e.g. 'X' in serial = 2023. Digits after letter = week + sequence. | Medium-High | —
[6 empty] | 2.0T | 24,000 | YXC24B21S
[6 empty] | 2.5T | 30,000 | YXC30B21S
[6 empty] | 3.0T | 36,000 | YXC36B21S
[6 empty] | 3.5T | 42,000 | YXC42B21S
[6 empty] | 4.0T | 48,000 | YXC48B21S
[6 empty] | 5.0T | 60,000 | YXC60B21S
York | Johnson Controls / Coleman, Heil, Luxaire | Affinity | Mid | R-410A | TXV | 2.0T | 24,000 | YXF24B21S | Same letter-year format. | Medium-High | —
[6 empty] | 2.5T | 30,000 | YXF30B21S
[6 empty] | 3.0T | 36,000 | YXF36B21S
[6 empty] | 4.0T | 48,000 | YXF48B21S
[6 empty] | 5.0T | 60,000 | YXF60B21S
York | Johnson Controls / Coleman, Heil, Luxaire | YXV | Premium | R-410A | EEV | 2.0T | 24,000 | YXV20B21S024 | Same letter-year format. | Medium-High | —
[6 empty] | 3.0T | 36,000 | YXV20B21S036
[6 empty] | 4.0T | 48,000 | YXV20B21S048
[6 empty] | 5.0T | 60,000 | YXV20B21S060
Daikin | Daikin Industries / Goodman, Amana | DN Series | Entry | R-410A | Piston | 1.5T | 18,000 | DX14SA018 | Same as Goodman YYWW format. Manufactured at Daikin Texas Technology Park, Waller TX. | Medium-High | —
[6 empty] | 2.0T | 24,000 | DX14SA024
[6 empty] | 2.5T | 30,000 | DX14SA030
[6 empty] | 3.0T | 36,000 | DX14SA036
[6 empty] | 3.5T | 42,000 | DX14SA042
[6 empty] | 4.0T | 48,000 | DX14SA048
[6 empty] | 5.0T | 60,000 | DX14SA060
Daikin | Daikin Industries / Goodman, Amana | DX Series | Mid | R-410A | TXV | 2.0T | 24,000 | DX17SA024 | Same YYWW format. | Medium-High | —
[6 empty] | 2.5T | 30,000 | DX17SA030
[6 empty] | 3.0T | 36,000 | DX17SA036
[6 empty] | 4.0T | 48,000 | DX17SA048
[6 empty] | 5.0T | 60,000 | DX17SA060
Daikin | Daikin Industries / Goodman, Amana | Daikin Fit | Premium | R-410A | EEV | 2.0T | 24,000 | DZ14SA024 | Same format. Fit = side-discharge inverter system. | Medium-High | —
[6 empty] | 2.5T | 30,000 | DZ14SA030
[6 empty] | 3.0T | 36,000 | DZ17SA036
[6 empty] | 4.0T | 48,000 | DZ20SA048
[6 empty] | 5.0T | 60,000 | DZ20SA060
Bryant | Carrier Global / Carrier, Payne | Legacy | Entry | R-410A | Piston | 1.5T | 18,000 | 913SA018C3NA | Identical to Carrier serial# decode. WWYY or MMYY format. Carrier Enterprise parts. | High | carrier_comfort
[6 empty] | 2.0T | 24,000 | 913SA024C3NA
[6 empty] | 2.5T | 30,000 | 913SA030C3NA
[6 empty] | 3.0T | 36,000 | 913SA036C3NA
[6 empty] | 3.5T | 42,000 | 913SA042C3NA
[6 empty] | 4.0T | 48,000 | 913SA048C3NA
[6 empty] | 5.0T | 60,000 | 913SA060C3NA
Bryant | Carrier Global / Carrier, Payne | Preferred | Mid | R-410A | TXV | 2.0T | 24,000 | 127B024 | Identical to Carrier serial# decode. | High | carrier_performance
[6 empty] | 2.5T | 30,000 | 127B030
[6 empty] | 3.0T | 36,000 | 127B036
[6 empty] | 4.0T | 48,000 | 127B048
[6 empty] | 5.0T | 60,000 | 127B060
Bryant | Carrier Global / Carrier, Payne | Evolution | Premium | R-410A | EEV | 2.0T | 24,000 | 180B024 | Identical to Carrier serial# decode. | High | carrier_infinity
[6 empty] | 3.0T | 36,000 | 180B036
[6 empty] | 4.0T | 48,000 | 180B048
[6 empty] | 5.0T | 60,000 | 180B060
American Standard | Trane Technologies / Trane | Gold | Entry | R-410A | Piston | 1.5T | 18,000 | 4A7A4018H1000A | Identical to Trane serial# decode. Letter+week format. A=2011...R=2025. | High | trane_xr
[6 empty] | 2.0T | 24,000 | 4A7A4024H1000A
[6 empty] | 2.5T | 30,000 | 4A7A4030H1000A
[6 empty] | 3.0T | 36,000 | 4A7A4036H1000A
[6 empty] | 4.0T | 48,000 | 4A7A4048H1000A
[6 empty] | 5.0T | 60,000 | 4A7A4060H1000A
American Standard | Trane Technologies / Trane | Silver | Mid | R-410A | TXV | 2.0T | 24,000 | 4A7B4024J1000A | Same Trane decode. | High | trane_xl
[6 empty] | 3.0T | 36,000 | 4A7B4036J1000A
[6 empty] | 4.0T | 48,000 | 4A7B4048J1000A
[6 empty] | 5.0T | 60,000 | 4A7B4060J1000A
American Standard | Trane Technologies / Trane | Platinum | Premium | R-410A | EEV | 2.0T | 24,000 | 4A7V4024J1000A | Same Trane decode. | High | trane_xv
[6 empty] | 3.0T | 36,000 | 4A7V4036J1000A
[6 empty] | 4.0T | 48,000 | 4A7V4048J1000A
[6 empty] | 5.0T | 60,000 | 4A7V4060J1000A
Amana | Daikin / Goodman, Daikin | ASX | Entry | R-410A | Piston | 1.5T | 18,000 | ASX140181 | Same as Goodman YYWW format. Made in Waller TX. Lifetime compressor warranty. | Medium | goodman_gsx
[6 empty] | 2.0T | 24,000 | ASX140241
[6 empty] | 2.5T | 30,000 | ASX140301
[6 empty] | 3.0T | 36,000 | ASX140361
[6 empty] | 3.5T | 42,000 | ASX140421
[6 empty] | 4.0T | 48,000 | ASX140481
[6 empty] | 5.0T | 60,000 | ASX140601
Amana | Daikin / Goodman, Daikin | ASXC | Mid | R-410A | TXV | 2.0T | 24,000 | ASXC160241 | Same YYWW format. | Medium | goodman_gsxc
[6 empty] | 3.0T | 36,000 | ASXC160361
[6 empty] | 4.0T | 48,000 | ASXC160481
[6 empty] | 5.0T | 60,000 | ASXC160601
Amana | Daikin / Goodman, Daikin | ASXV | Premium | R-410A | EEV | 2.0T | 24,000 | ASXV9024 | Same YYWW format. | Medium | goodman_gsxv
[6 empty] | 3.0T | 36,000 | ASXV9036
[6 empty] | 4.0T | 48,000 | ASXV9048
[6 empty] | 5.0T | 60,000 | ASXV9060
Ruud | Rheem Mfg / Rheem | EcoNet Select | Entry | R-410A | Piston | 1.5T | 18,000 | UA14AJ018 | Same as Rheem decode. Decade+Year+Week format. | Medium | rheem_select
[6 empty] | 2.0T | 24,000 | UA14AJ024
[6 empty] | 2.5T | 30,000 | UA14AJ030
[6 empty] | 3.0T | 36,000 | UA14AJ036
[6 empty] | 4.0T | 48,000 | UA14AJ048
[6 empty] | 5.0T | 60,000 | UA14AJ060
Ruud | Rheem Mfg / Rheem | EcoNet Achiever | Mid | R-410A | TXV | 2.0T | 24,000 | UA17AJ024 | Same Rheem decode. | Medium | rheem_achiever
[6 empty] | 3.0T | 36,000 | UA17AJ036
[6 empty] | 4.0T | 48,000 | UA17AJ048
[6 empty] | 5.0T | 60,000 | UA17AJ060
Ruud | Rheem Mfg / Rheem | EcoNet Ultra | Premium | R-410A | EEV | 2.0T | 24,000 | UA20AJ024 | Same Rheem decode. | Medium | rheem_prestige
[6 empty] | 3.0T | 36,000 | UA20AJ036
[6 empty] | 4.0T | 48,000 | UA20AJ048
[6 empty] | 5.0T | 60,000 | UA20AJ060
Heil | Johnson Controls / York, Coleman | QuietComfort | Entry | R-410A | Piston | 1.5T | 18,000 | HCA318GKA | Same as York letter-year decode. A=2004 through Z=2025. Letter in serial = year. | Medium | york_lx
[6 empty] | 2.0T | 24,000 | HCA324GKA
[6 empty] | 2.5T | 30,000 | HCA330GKA
[6 empty] | 3.0T | 36,000 | HCA336GKA
[6 empty] | 4.0T | 48,000 | HCA348GKA
[6 empty] | 5.0T | 60,000 | HCA360GKA
Heil | Johnson Controls / York, Coleman | QuietComfort Deluxe | Mid-Prem | R-410A | TXV | 2.0T | 24,000 | HCA318GKA024 | Same York decode. | Medium | york_affinity
[6 empty] | 3.0T | 36,000 | HCA318GKA036
[6 empty] | 4.0T | 48,000 | HCA318GKA048
[6 empty] | 5.0T | 60,000 | HCA318GKA060
Coleman | Johnson Controls / York, Heil | Echelon | Entry | R-410A | Piston | 1.5T | 18,000 | TC14B18S | Same as York/Heil letter-year serial decode. | Medium-Low | york_lx
[6 empty] | 2.0T | 24,000 | TC14B24S
[6 empty] | 2.5T | 30,000 | TC14B30S
[6 empty] | 3.0T | 36,000 | TC14B36S
[6 empty] | 4.0T | 48,000 | TC14B48S
[6 empty] | 5.0T | 60,000 | TC14B60S
Coleman | Johnson Controls / York, Heil | Echelon Deluxe | Mid | R-410A | TXV | 2.0T | 24,000 | TC18B24S | Same York decode. | Medium-Low | york_affinity
[6 empty] | 3.0T | 36,000 | TC18B36S
[6 empty] | 4.0T | 48,000 | TC18B48S
[6 empty] | 5.0T | 60,000 | TC18B60S
Payne | Carrier Global / Carrier, Bryant | Payne Entry | Entry | R-410A | Piston | 1.5T | 18,000 | PA14NA018000C | Identical to Carrier serial# decode. WWYY or MMYY format. | Medium-Low | carrier_comfort
[6 empty] | 2.0T | 24,000 | PA14NA024000C
[6 empty] | 2.5T | 30,000 | PA14NA030000C
[6 empty] | 3.0T | 36,000 | PA14NA036000C
[6 empty] | 4.0T | 48,000 | PA14NA048000C
[6 empty] | 5.0T | 60,000 | PA14NA060000C
Payne | Carrier Global / Carrier, Bryant | Payne Mid | Mid | R-410A | TXV | 2.0T | 24,000 | PA16NA024000C | Identical to Carrier serial# decode. | Medium-Low | carrier_performance
[6 empty] | 3.0T | 36,000 | PA16NA036000C
[6 empty] | 4.0T | 48,000 | PA16NA048000C
[6 empty] | 5.0T | 60,000 | PA16NA060000C
Mitsubishi Electric | Mitsubishi Electric Corp | M-Series MSZ | Standard | R-410A | EEV | 0.75T | 9,000 | MSZ-GL09NA-U1 | Format: Factory code (3 chars) + YYMM + seq. e.g. 'E231200001' = Dec 2023. Mini-split — different diagnostic approach from central AC. | Medium-Low | —
[6 empty] | 1.0T | 12,000 | MSZ-GL12NA-U1
[6 empty] | 1.5T | 18,000 | MSZ-GL18NA-U1
[6 empty] | 2.0T | 24,000 | MSZ-GL24NA-U1
[6 empty] | 2.5T | 30,000 | MSZ-GL30NA-U1
[6 empty] | 3.0T | 36,000 | MSZ-GS36NA-U1
Mitsubishi Electric | Mitsubishi Electric Corp | Hyper-Heat H2i | Premium | R-410A | EEV | 0.75T | 9,000 | MSZ-FH09NA | Same decode. H2i heats to -13°F. Rare in Houston. | Medium-Low | —
[6 empty] | 1.0T | 12,000 | MSZ-FH12NA
[6 empty] | 1.5T | 18,000 | MSZ-FH18NA
[6 empty] | 2.0T | 24,000 | MSZ-FH24NA
[6 empty] | 2.5T | 30,000 | MXZ-3C30NAHZ

## Serial # Decoder
SnapAI — Serial Number Age Decoder by Brand ¦ Use to determine unit age from nameplate serial number
Brand(s) | Serial # Format | How to Find Age | Example | Age Calc Example | Notes
Carrier, Bryant, Payne | Pre-2015: WWYY + seq (e.g. 0614XXXXX) Post-2015: 2-letter factory + MMYY + seq | Pre-2015: digits 1-2 = week, 3-4 = year Post-2015: digits 3-4 = month, 5-6 = year (after factory prefix) | 0614XXXXXXX 3020XXXXXXX (factory code omitted) | 0614 → Week 06 of 2014 → Feb 2014 3020 → Month 30? — see post-2015 note | Post-2015 Carrier: first 2 alpha chars are factory (e.g. EA, PH). Digits after = MMYY. System age = current year minus serial year.
Trane, American Standard | Letter + 2-digit week + 5-digit seq e.g. N1500001 | 1st character = year letter. A=2011, B=2012, C=2013, D=2014, E=2015, F=2016, G=2017, H=2018, J=2019, K=2020, L=2021, M=2022, N=2023, P=2024, R=2025 | N1500001 K2300045 | N = 2023, Week 15 → Apr 2023 K = 2020, Week 23 → Jun 2020 | Trane skip letter 'I' and 'O' to avoid confusion with 1 and 0. Same decode for American Standard (identical units).
Goodman, Amana, Daikin (Waller TX) | YYWW + seq (8-10 chars) e.g. 2315XXXXXXX | Digits 1-2 = year (last 2 digits), Digits 3-4 = week number | 2315XXXXXXX 1942XXXXXXX | 23+15 → 2023, Week 15 → Apr 2023 19+42 → 2019, Week 42 → Oct 2019 | Most straightforward decode in the industry. All three brands share Waller TX manufacturing. Parts interchangeable across Goodman/Amana/Daikin residential lines.
Rheem, Ruud | Decade letter + Year digit + WW + seq e.g. H315XXXXXXX | 1st char = decade: F=2000s, G=2010s, H=2020s 2nd char = year within decade (0-9) Chars 3-4 = week | H315XXXXXXX G718XXXXXXX | H=2020s, 3=2023, Week 15 → Apr 2023 G=2010s, 7=2017, Week 18 → May 2017 | Ruud identical to Rheem decode. Both use same manufacturing plants.
York, Heil, Coleman, Luxaire | Alpha char + week + 6-digit seq e.g. X1500001 | 1st character = year. A=2004,B=2005,C=2006,D=2007,E=2008,F=2009,G=2010,H=2011,J=2012,K=2013,L=2014,M=2015,N=2016,P=2017,R=2018,S=2019,T=2020,U=2021,V=2022,W=2023,X=2024,Y=2025 | X1500001 S2300001 | X = 2024, Week 15 → Apr 2024 S = 2019, Week 23 → Jun 2019 | York/JCI skip 'I', 'O', 'Q'. All Johnson Controls family brands (Heil, Coleman, Luxaire) use same decode.
Lennox, Armstrong Air | YYYYWW + seq or YYYYMM + seq e.g. 202315XXXXXXX | First 4 digits = full year, digits 5-6 = week or month | 202315XXXXXXX 202207XXXXXXX | 2023+15 → 2023, Week 15 → Apr 2023 2022+07 → 2022, July 2022 | Newer Lennox units use YYYYWW (week-based). Older pre-2010 units used a different letter-number system. Heil (now Johnson Controls) is separate from Lennox.
Mitsubishi Electric | Factory code (3 alpha) + YYMM + seq | Characters 4-5 = year (2-digit), 6-7 = month | E23120001 | E = factory, 23=2023, 12=December → Dec 2023 | Mini-split focused. Different from central AC diagnostics. MXZ = multi-zone outdoor unit. MSZ = single-zone head unit.

## Parts & Pricing
SnapAI — Parts & Pricing Reference ¦ Houston, TX Market ¦ 2026 Rates ¦ Wholesale + Retail + Installed
Part Name | Category | Fault Card(s) | Wholesale Cost | Retail Part Cost | Total Installed (Houston) | Labor Hours | Tech Notes
Run Capacitor (Single) — Compressor or Fan | electrical | #1, #4 | $8–$25 | $20–$55 | $150–$300 (typ $225) | 0.4–0.6 hrs | Single round run capacitor. Rated 370V or 440V. Common values: 20, 25, 30, 35, 40, 45, 50, 55, 60 MFD.
Dual Run Capacitor (Compressor + Fan) | electrical | #1, #4 | $12–$35 | $25–$65 | $175–$325 (typ $240) | 0.4–0.6 hrs | Oval dual-run capacitor. Replaces both compressor and fan motor caps in one unit. Most common residential part.
Contactor (2-pole 30–40A) | electrical | #3 | $10–$30 | $20–$55 | $175–$325 (typ $235) | 0.4–0.6 hrs | Standard 2-pole contactor for residential AC outdoor unit. 24V coil, 30A or 40A contacts.
Contactor + Dual Run Capacitor (Combo Job) | electrical | #1, #3 | — | — | $275–$450 (typ $350) | 0.6–0.9 hrs | Most common combination job — tech often replaces both at same visit.
Condenser Fan Motor (Outdoor Unit) | motors | #4 | $45–$120 | $80–$220 | $300–$575 (typ $425) | 0.8–1.5 hrs | OEM or aftermarket condenser fan motor. Typical specs: 1/4 HP, 825 RPM, 208/230V single-phase.
Blower Motor — PSC (Permanent Split Capacitor) | motors | #4 | $50–$130 | $85–$200 | $325–$600 (typ $450) | 1.5–2.5 hrs | Standard blower motor for air handler. Multiple speed taps (L/M/H). Common in pre-2020 units.
Blower Motor — ECM (Electronically Commutated Motor) | motors | #4 | $140–$400 | $220–$480 | $500–$900 (typ $675) | 2.0–3.0 hrs | Variable-speed ECM motor. Found in higher-efficiency units (2016+). Must match control module.
Condensate Drain Flush (Chemical + Labor) | maintenance | #5 | — | — | $120–$225 (typ $165) | 0.5–0.75 hrs | Chemical flush of condensate drain line. Includes flush tablet/treatment left in pan.
Drain Pan Cleaning + Flush | maintenance | #5 | — | — | $145–$250 (typ $185) | 0.75–1.25 hrs | Full drain pan clean-out with algaecide treatment. Includes flush line.
Condensate Pan Treatment Tablet | maintenance | #5 | — | $8–$20 | $18–$35 (typ $25) | 0.1–0.1 hrs | Slow-release pan tablet. Prevents algae regrowth. Added at end of every drain service call.
Air Filter — 1-inch Standard (MERV 8) | maintenance | #2, #9 | — | $10–$28 | $18–$45 (typ $30) | 0.15–0.25 hrs | Standard 1-inch pleated filter. MERV 8. Most common Houston residential size.
Air Filter — 4-5-inch Media (MERV 11–13) | maintenance | #2, #9 | — | $28–$80 | $45–$120 (typ $75) | 0.15–0.25 hrs | High-capacity media filter. Lasts 6–12 months. Requires special media cabinet.
Condenser Coil Cleaning (Outdoor) | maintenance | #14 | — | — | $145–$285 (typ $195) | 0.75–1.5 hrs | Chemical coil cleaner + rinse. Removes dirt, grass clippings, fin blockage. Top Houston upsell on service calls.
Evaporator Coil Cleaning (Indoor/Air Handler) | maintenance | #14, #9 | — | — | $185–$375 (typ $265) | 1.25–2.0 hrs | No-rinse evaporator coil cleaner spray. More labor due to access inside air handler.
Refrigerant R-410A (per pound, add-on) | refrigerant | #8, #9, #15, #17 | — | — | $80–$150 (typ $110) | — | R-410A Puron refrigerant. Price shown is retail installed per pound added. Includes recovery/handling fee.
Refrigerant R-22 (per pound, reclaimed only) | refrigerant | #8 | — | — | $250–$400 (typ $320) | — | R-22 Freon. Reclaimed only since 2020 US ban. Very expensive and scarce. Recommend system replacement if R-22 unit needs
Refrigerant Recovery + Evacuation + Full Recharge | refrigerant | #8, #15, #12, #17 | — | — | $225–$500 (typ $350) | 0.75–1.25 hrs | Full system recovery, evacuation (300 microns), and recharge to factory spec. Required after any refrigerant-side repair
Refrigerant Leak Search (Electronic + UV Dye) | refrigerant | #8 | — | — | $150–$325 (typ $225) | 1.0–2.0 hrs | Electronic leak detector + UV dye injection to find leak source. Labor only — refrigerant billed separately.
UV Dye Injection | refrigerant | #8 | — | — | $85–$165 (typ $120) | 0.25–0.5 hrs | UV tracer dye injected into refrigerant circuit. Leak glows under UV light. Evidence photo value for homeowner PDF.
TXV Valve (Thermostatic Expansion Valve) | refrigerant_controls | #15 | $45–$160 | $85–$250 | $375–$750 (typ $525) | 2.5–4.5 hrs | TXV metering device at indoor coil. Must match tonnage and refrigerant. Requires refrigerant recovery/recharge.
Fixed Orifice / Piston Metering Device | refrigerant_controls | #15 | $8–$25 | $18–$55 | $275–$525 (typ $385) | 2.0–3.5 hrs | Fixed orifice (piston) metering device. Bore size determines refrigerant flow. Must match tonnage exactly.
Reversing Valve (Heat Pump) | refrigerant_controls | #12 | $75–$220 | $120–$300 | $450–$875 (typ $625) | 3.5–5.5 hrs | 4-way reversing valve — heat pump only. Controls heat/cool mode switch. Requires full refrigerant handling.
Control Board (Outdoor or Indoor Unit) | controls | #7 | $60–$250 | $100–$350 | $350–$700 (typ $500) | 0.75–1.5 hrs | Main control/defrost board. Brand-specific — must match model series. Outdoor or indoor board billed separately.
Thermostat (Programmable / Smart) | controls | #7 | — | $50–$350 | $130–$500 (typ $275) | 0.5–1.0 hrs | Replacement thermostat. Basic programmable ($50–100) to smart WiFi ($150–350).
Hot Surface Ignitor (Gas Furnace) | heating | #11 | $12–$45 | $22–$70 | $165–$325 (typ $235) | 0.5–0.75 hrs | Silicon carbide or silicon nitride ignitor. Specific to furnace model. Very fragile — handle with care.
Flame Sensor Rod (Gas Furnace) | heating | #11 | $5–$18 | $10–$30 | $120–$235 (typ $165) | 0.4–0.65 hrs | Stainless steel sensing rod. Often cleanable with steel wool before replacement. Very low cost part.
Evaporator Coil (2–3 Ton) | coils | #19, #9 | $280–$580 | $450–$900 | $900–$1650 (typ $1250) | 3.5–5.5 hrs | Replacement A-coil or slab coil for air handler. Must match system tonnage, refrigerant, and TXV/piston type.
Evaporator Coil (4–5 Ton) | coils | #19, #9 | $420–$820 | $650–$1200 | $1300–$2400 (typ $1750) | 4.5–6.5 hrs | Large evaporator coil. Requires more labor and refrigerant for recharge.
Condenser Coil (Outdoor Unit) | coils | #14, #19 | $280–$720 | $450–$1100 | $850–$1900 (typ $1350) | 2.5–4.5 hrs | Replacement condenser coil. OEM or aftermarket. Requires refrigerant recovery/recharge.
Compressor Replacement — 2 Ton | compressor | #10 | $280–$480 | $420–$680 | $950–$1550 (typ $1200) | 3.5–5.5 hrs
Compressor Replacement — 3 Ton | compressor | #10 | $350–$550 | $520–$780 | $1100–$1750 (typ $1400) | 4.0–6.0 hrs
Compressor Replacement — 4 Ton | compressor | #10 | $420–$680 | $620–$950 | $1300–$2100 (typ $1650) | 4.5–6.5 hrs
Compressor Replacement — 5 Ton | compressor | #10 | $520–$850 | $750–$1150 | $1550–$2500 (typ $2000) | 5.0–7.0 hrs
Ductwork Repair (accessible section) | ductwork | #13 | — | — | $250–$550 (typ $375) | 1.0–2.5 hrs | Seal and repair accessible duct section. Mastic sealant + foil tape. Attic ductwork is typical.
Wiring / Terminal Repair | electrical | #6, #16 | — | — | $145–$375 (typ $225) | 0.5–1.5 hrs | Repair or replace damaged low-voltage or line-voltage wiring. Terminal replacement, heat-shrink splices.
Terminal Cleaning + Retorque (Card #16) | electrical | #16 | — | — | $125–$250 (typ $175) | 0.5–1.0 hrs | Clean oxidized/loose terminals, retorque to spec, verify voltage drop. No parts in most cases.
Service Call / Diagnostic Fee | service | all | — | — | $85–$175 (typ $125) | 0.5–1.0 hrs | Standard diagnostic fee. Many Houston companies waive if repair is booked.
Annual Service / Tune-Up | service | S | — | — | $120–$199 (typ $155) | 1.0–1.5 hrs | Annual preventive maintenance. Base labor + drain flush tablet. Findings add as separate line items.

## Error Code DB Summary
SnapAI Error Code DB — 159 Codes, 8 Brand Families ¦ ac_data_repo.json → error_code_db
Brand Family | System Type | Code | Meaning | Action | Routes to Card
Carrier/Bryant/Payne | LED Flash | 4 flash | High limit trip — overheating | Check filter, blower, airflow | #2
Carrier/Bryant/Payne | LED Flash | 8 flash | Ignitor fault | Measure ignitor resistance; replace if open | #7
Carrier/Bryant/Payne | Infinity (communicating) | 173 | Low pressure switch open | Check charge; check metering device | #8
Carrier/Bryant/Payne | Infinity (communicating) | 176 | High pressure switch open | Check condenser coil, fan, charge | #8
Carrier/Bryant/Payne | Infinity (communicating) | 184 | Compressor trip / lockout | Hard start kit or compressor replacement | #13
Trane/American Standard | LED Flash | 4 flash | Open high limit — overheating | Check filter, blower, airflow | #2
Trane/American Standard | LED Flash | 3 flash | Vent pressure switch stuck open | Check inducer, vent, pressure switch tubing | #7
Trane/American Standard | ComfortLink (communicating) | 101 | High pressure lockout | Check condenser coil, fan, charge | #8
Trane/American Standard | ComfortLink (communicating) | 102 | Low pressure lockout | Check charge; check TXV/piston | #8
Trane/American Standard | ComfortLink (communicating) | 184 | Compressor lockout | Evaluate compressor; hard start kit | #13
Goodman/Amana/Daikin | LED Flash | 4 flash | Open limit circuit — overheating | Replace filter; check blower motor cap | #2
Goodman/Amana/Daikin | LED Flash | 1 flash | Furnace lockout — 3 failed ignition attempts | Check gas, ignitor, flame sensor | #7
Goodman/Amana/Daikin | ComfortNet (communicating) | E4 | High pressure lockout | Check condenser coil, fan motor, charge | #8
Goodman/Amana/Daikin | ComfortNet (communicating) | E5 | Low pressure lockout | Check charge; check metering device | #8
Goodman/Amana/Daikin | ComfortNet (communicating) | E9 | Compressor overload — high current | Check capacitor; check amp draw vs RLA | #1
Rheem/Ruud | LED Flash | 4 flash | Condensate float switch tripped | Clear drain; flush; check float switch | #5
Rheem/Ruud | LED Flash | 6 flash | Low supply air temp — coil icing | Check charge, airflow, filter; look for ice | #8
Rheem/Ruud | EcoNet (communicating) | 40 | High pressure switch fault | Check condenser coil, fan, charge | #8
Rheem/Ruud | EcoNet (communicating) | 41 | Low pressure switch fault | Check charge; check metering device | #8
Rheem/Ruud | EcoNet (communicating) | 80 | Insufficient airflow | Check filter, coil, duct static pressure | #2
York/Heil/Coleman | LED/Display | E1 | Indoor/outdoor comm fault | Check communication wiring and boards | #7
York/Heil/Coleman | LED/Display | EE | Water level alarm — drain overflow | Clear drain; replace float switch | #5
York/Heil/Coleman | LED/Display | F4 | Discharge temp overheat protection | Check charge, condenser airflow | #8
York/Heil/Coleman | LED/Display | F0 | Overload protection activation | Check amps; check capacitor; allow cool-down | #1
Lennox | LED Flash | 3 flash | High limit switch tripped | Check filter, airflow, blower cap | #2
Lennox | iComfort (communicating) | 312 | Reduced airflow alert — dirty filter | Replace filter; check coil and static pressure | #2
Lennox | iComfort (communicating) | A1025 | Compressor start failure | Check capacitor; check compressor windings | #1
Lennox | iComfort (communicating) | E6 | High pressure lockout | Check condenser coil, fan, charge | #8
Mitsubishi (mini-split) | Indoor display | U4 | Comm failure indoor→outdoor (MOST COMMON ~40%) | Check outdoor disconnect, comm wire, voltage | #7
Mitsubishi (mini-split) | Indoor display | E6 | Indoor PCB / display comm error | Check PCB wiring; replace PCB if needed | #7
Mitsubishi (mini-split) | Indoor display | P6 | Compressor lockout — repeat trips | Check charge, voltage, compressor efficiency | #13
Mitsubishi (mini-split) | Indoor display | P8 | Coil temp fault — coil icing or overtemp | Check charge; check indoor coil for ice/dirt | #8
Daikin (mini-split) | Indoor display | U4 | Indoor/outdoor comm fault | Check comm cable; check both PCBs | #7
Daikin (mini-split) | Indoor display | E3 | High pressure switch protection | Check condenser coil, fan, charge | #8
Daikin (mini-split) | Indoor display | A3 | Drain system fault | Clear drain; check float switch/pump | #5
Daikin (mini-split) | Indoor display | U0 | Low refrigerant charge detected | Leak check; evacuate and recharge | #8