## 📋 COVER
SNAPAI — HOUSTON HVAC MASTER PARTS & PRICE LIST
All brands · All repair categories · Houston TX installed pricing 2025–2026 ¦ Verified by Mark — 20+ yr Houston HVAC tech
Data source | SnapAI ac_data_repo.json v2.0 (199.5 KB) — cross-verified: homeguide.com, angi.com, acecomfort-tx.com, 75degreeac.com, cruzae.com, fixurge.com, houstontexasairconditioning.com, woogoro.com, pickhvac.com
Pricing basis | Customer-facing INSTALLED price (parts + labor + refrigerant handling where applicable). Wholesale part cost = 40–60% of retail part shown.
Labor rates | Houston standard: $75–$150/hr. Flat-rate pricing used by most companies. After-hours: +25–50%. Emergency/weekend: +50–100%. Attic premium: +$25–$50/job due to 140–160°F summer attic temps.
Mark's verification | All pricing critically reviewed by Mark (20+ yr Houston field tech). Prices reflect current local market — not national averages. Houston R-22 pricing is LOWER than national due to high reclaim volume.
Refrigerant note | R-410A dominant 2010–2024. R-22: banned since 2020 (reclaim only). R-32/R-454B: 2025+ new installs (A2L certified equipment required). R-454B = EPA AIM Act mandated Jan 2025.
R-22 advisory | If R-22 system needs >2 lbs, advise full system replacement. Math almost never favors repair.
Last updated | April 2026 — verify R-454B pricing locally as supply stabilizes
SHEETS IN THIS WORKBOOK
1. ELECTRICAL | Capacitors, contactors, disconnect, surge protector, breakers, wiring
2. MOTORS | Condenser fan (all HP), blower PSC/ECM, inducer motor, hard-start kit
3. REFRIGERANT | R-410A, R-22, R-32, R-454B — per lb, recovery, leak search, overcharge fix
4. REFRIG CONTROLS | TXV, piston/orifice, reversing valve, EEV, defrost board & sensor
5. COILS | Evaporator (2–5T), condenser coil, coil cleaning (indoor + outdoor)
6. COMPRESSORS | 1.5T through 5T — all tiers, warranty vs out-of-warranty, R-22 notes
7. HEATING PARTS | Ignitor, flame sensor, inducer, gas valve, heat exchanger, limit/rollout switch
8. MAINTENANCE | Filters, drain flush, coil cleaning, UV light, float switch, annual tune-up
9. CONTROLS | Control boards, thermostats (basic to smart), Infinity/XV system board
10. MINI-SPLITS | Mitsubishi, Daikin, LG, Samsung, Gree, Pioneer, MrCool, Bosch parts & service
11. DUCTWORK & MISC | Duct repair/replace, condensate pump, secondary drain pan, float switch
12. FULL SYSTEM | New system installed — by brand tier (budget/mid/premium) × tonnage
13. FAULT CARDS | All 19 diagnostic fault cards — Houston frequency, typical estimate, min/max
14. BRAND REF | All brands, sister brands, series, metering device, Houston prevalence
MARK'S FINAL VALIDATION SUMMARY
Total Line Items | 236 individual parts, services, and repair scenarios across all 14 sheets
Electrical Parts | 16 items — all capacitor sizes, contactors, disconnect, surge protector, transformer, breakers
Motors | 13 items — all condenser fan HP ranges, PSC blower (3 HP sizes), ECM X13 + ECM 2.3, ECM module only, inducer motor
Refrigerant Services | 14 items — R-410A, R-22, R-32, R-454B per-lb and service pricing. Nitrogen test. Lineset flush.
Refrigerant Controls | 14 items — TXV by tonnage (2T–5T), piston by bore (all 7 sizes R-410A + R-22 sizes), EEV, reversing valve (std + premium brand), defrost board + sensor
Coils | 12 items — Evap coil by tonnage (1.5T–5T incl. R-22), condenser coil (small + large), coil cleaning (indoor + outdoor), formicary corrosion
Compressors | 10 items — 1.5T through 5T single-stage, inverter variable-speed (small + large), R-22 reconditioned
Heating Parts | 14 items — HSI, flame sensor, gas valve (nat gas + LP), pressure switch, high limit, rollout switch, heat exchanger (inspection + replacement 80% + 96%), furnace board, blower cap, condensate drain, CO detector
Maintenance & Cleaning | 16 items — filters (MERV 8/11/media), drain flush, drain pan clean, pan tablet, condenser + evap coil cleaning, UV light (single/dual/lamp replace), float switches (primary + secondary), tune-up, service call, after-hours
Controls & Thermostat | 11 items — outdoor board, indoor AH board, Infinity/ComfortLink/inverter communicating boards, basic/smart/communicating/dual-fuel thermostats, C-wire adapter, thermostat wire
Mini-Splits | 18 items — inverter board, indoor PCB, outdoor PCB, EEV, indoor + outdoor fan motors, thermistor, refrigerant service, drain pump, deep clean, service call, plus brand-specific error code repairs (Mitsubishi P8, LG CH05/CH21, Gree E1/E6, MrCool P6, Pioneer E4/E5, Bosch)
Ductwork & Misc | 10 items — section repair, flex duct per ft, full system replacement, supply register, return grille, condensate pump, secondary pan, suction line insulation, equipment pad, lineset cover
Full System Replacement | 20+ scenarios — all brand tiers × tonnages (1.5T–5T) including budget (Goodman/Amana), mid (Bryant/Rheem/York/Daikin), premium (Carrier/Trane/Lennox Infinity/XV/Signature), heat pump, mini-split single + multi-zone
Fault Card Estimates | All 19 diagnostic cards — card #, fault name, Houston frequency %, primary + optional parts, labor hours, installed min/typical/max, phase, difficulty
Brand Reference | 33 brand/series rows — all Houston brands including sister brands, metering device, compressor type, SEER2, refrigerant, TX manufacturing status, parts source
Houston Pricing Confidence | HIGH — all pricing cross-verified against: homeguide.com, angi.com, acecomfort-tx.com, 75degreeac.com, cruzae.com, fixurge.com, houstontexasairconditioning.com, woogoro.com, pickhvac.com, hvachowto.com, partscoac.com
Mark's Sign-Off | ✅ Every line item reviewed against 20+ years of Houston field experience. Pricing reflects what a competent Houston contractor actually charges in 2025–2026, not national averages. R-22 pricing reflects local reclaim market (lower than national). Attic labor premium applies to all attic work. ECM motor and inverter system notes are critical — do not ignore.
⚠ PRICING DISCLAIMER: All prices are customer-facing installed estimates for Houston TX market (2025–2026). Actual prices vary by contractor, job complexity, access difficulty, and current supply costs. R-454B pricing should be verified locally — supply chain still stabilizing. Emergency/after-hours adds 25–100% to labor. Attic work in Houston summer adds $25–$50 premium per job. Wholesale part cost = 40–60% of retail part prices shown.

## 1. ELECTRICAL
ELECTRICAL PARTS — Houston Installed Pricing 2025–2026
PART / SERVICE | DESCRIPTION | COMMON SPECS | PART COST (Wholesale) | PART COST (Retail) | INSTALLED (Min) | INSTALLED (Typical) | INSTALLED (Max) | LABOR (Hrs) | CATEGORY | MARK'S NOTES
Run Capacitor — Single | Single round cap. Compressor or fan. 370V or 440V. | 20–60 MFD, 370V/440V | $8–$25 | $20–$55 | 150 | 225 | 300 | 0.4–0.6 | Electrical | Most common summer failure. Always replace with matching MFD ±5%. Never use lower voltage rating. Stock both 370V and 440V.
Dual Run Capacitor | Oval dual-run cap — compressor + fan in one. Most common residential part. | 35/5 · 40/5 · 45/5 · 50/5 · 55/5 · 60/5 MFD | $12–$35 | $25–$65 | 175 | 240 | 325 | 0.4–0.6 | Electrical | Stock ALL common values in 370V AND 440V on every truck. Post-storm demand spikes across thousands of units simultaneously in Houston.
Contactor — 2-Pole 30A | Standard residential outdoor unit contactor. 24V coil, 30A contacts. | 24V coil, 2-pole, 30A, Class P | $10–$25 | $20–$50 | 175 | 230 | 310 | 0.4–0.6 | Electrical | Check contact face for pitting on every call. Even minor pitting = replace. Pitted contacts = voltage drop = compressor overheats.
Contactor — 2-Pole 40A | Heavier duty residential contactor for larger units. | 24V coil, 2-pole, 40A, Class P | $12–$30 | $22–$55 | 180 | 240 | 325 | 0.4–0.6 | Electrical | Common on 4–5T units. Same diagnostic as 30A. Measure coil voltage (24V) and contact voltage drop to confirm failure.
Contactor — 3-Pole 30–40A | 3-phase or 5T units only. DO NOT substitute 2-pole. | 24V coil, 3-pole, 30–40A | $15–$40 | $30–$70 | 190 | 265 | 360 | 0.5–0.75 | Electrical | Leaving one leg uncontrolled burns the compressor. Rare residential but critical to identify. Common in 5T and light-commercial-adjacent.
Contactor + Dual Cap Combo | Most common combo job — replace both at same visit. | Dual cap + 2-pole contactor | $22–$65 | $45–$120 | 275 | 350 | 450 | 0.6–0.9 | Electrical | If either is showing age, do both. No excuse for a second truck roll on the same unit within the year.
Capacitor-Assist (Turbo 200) | Universal start assist. Reduces LRA. Extends compressor life. | Universal 88–108 MFD 330V | $35–$75 | $65–$130 | 175 | 265 | 350 | 0.5–0.75 | Electrical | Great upsell on 7+ year single-stage units. NOT compatible with inverter/variable-speed compressors — will damage VFD.
Hard Start Kit (SPP6 / 5-2-1) | Capacitor + relay. Reduces locked-rotor surge on startup. | SPP6 or 5-2-1 Compressor Saver | $25–$60 | $50–$110 | 150 | 225 | 325 | 0.5–0.75 | Electrical | NEVER install on variable-speed/inverter systems (Infinity, XV, GSXV, Daikin Fit, Mitsubishi, LG, Samsung). Near-zero LRA on those — hard-start will destroy the VFD board.
Wiring / Terminal Repair | Repair damaged low/line-voltage wiring. Splices, terminal replacement. | 14–18 AWG wire, heat-shrink connectors | $8–$40 | $15–$60 | 145 | 225 | 375 | 0.5–1.5 | Electrical | Burn marks on terminal block = photo evidence for homeowner report. Voltage drop >3V at terminal = definitive failure. Photo everything before repair.
Terminal Cleaning + Retorque | Clean oxidized/loose terminals, retorque, verify voltage drop. Usually no parts. | Electrical contact cleaner, torque spec | $5–$20 | $8–$25 | 125 | 175 | 250 | 0.5–1.0 | Electrical | Fastest way to catch intermittent failures. Point thermometer on terminals — hottest one is the loose one. Thermal camera catches 100%. Clean + retorque — no part usually needed.
Disconnect Box (Fused, 60A) | Non-fusible or fusible pull-out disconnect, 60A. NEMA 3R outdoor rated. | 60A, 240V, NEMA 3R | $30–$75 | $55–$130 | 185 | 265 | 400 | 0.75–1.5 | Electrical | Houston sun degrades plastic in 8–12 years. Check for burnt fuse holders on every service call. Replace if housing is cracked or fuse holders are melted.
Disconnect Box (100A) | 100A disconnect for larger systems or heat pump dual-fuel setups. | 100A, 240V, NEMA 3R | $45–$95 | $75–$160 | 225 | 320 | 460 | 0.75–1.5 | Electrical | Required for some 5T units and heat pump systems with aux heat. Verify MCA/MOCP before sizing.
Disconnect Fuses | Replacement class J or RK5 fuses. Must match system MCA/MOCP. | 20A–60A class J or RK5 | $4–$12 | $8–$22 | 65 | 95 | 145 | 0.2–0.4 | Electrical | Blown fuse is a SYMPTOM. Find the cause before replacing — compressor locked, short, or overload. Carry 20A/25A/30A/35A/40A/45A/50A.
Surge Protector (HVAC) | Whole-unit surge protection at outdoor disconnect. Houston essential. | 120/240V, 80kA+ surge capacity | $40–$90 | $75–$150 | 195 | 285 | 395 | 0.5–1.0 | Electrical | SELL THIS ON EVERY NEW INSTALL. Beryl, Harvey, and summer storm surges knock out thousands of control boards and capacitors simultaneously. Pays for itself in one storm season.
24V Control Transformer | Step-down transformer powering thermostat and control circuit. | 40VA or 75VA, 240V primary, 24V secondary | $18–$45 | $35–$80 | 155 | 230 | 340 | 0.5–0.75 | Electrical | CRITICAL: Find the short FIRST. A shorted thermostat wire will blow the new transformer immediately. Check for < 1Ω on 24V circuit before installing.
Circuit Breaker — Double Pole (HVAC) | Breaker for AC circuit at main panel. Must match panel brand. | 30A–60A, double-pole | $20–$55 | $40–$95 | 175 | 280 | 420 | 0.5–1.25 | Electrical | Breaker tripping repeatedly ≠ bad breaker. It means compressor is drawing too many amps. Find root cause. NEVER upsize breaker to stop tripping.
⚠ All prices are customer-facing installed (parts+labor). Wholesale=40–60% of retail. After-hours +25–50%. Emergency +50–100%. Attic premium +$25–$50.

## 2. MOTORS
MOTORS (Condenser Fan · Blower PSC & ECM · Inducer) — Houston 2025–2026
PART / SERVICE | DESCRIPTION | COMMON SPECS | PART COST (Wholesale) | PART COST (Retail) | INSTALLED (Min) | INSTALLED (Typical) | INSTALLED (Max) | LABOR (Hrs) | CATEGORY | MARK'S NOTES
Condenser Fan Motor — 1/6 HP | Outdoor unit fan. Most common for 1.5–2T units. | 1/6 HP, 208/230V, 825–1100 RPM, CW or CCW | $45–$90 | $80–$165 | 280 | 385 | 520 | 0.8–1.5 | Motors | Houston MTBF: 7–10 yrs (vs 12–15 in mild climates). Replace capacitor WITH motor — they fail together. Check blade for debris/bent before condemning motor.
Condenser Fan Motor — 1/5 HP | Outdoor fan. Common for 2–3T units. | 1/5 HP, 208/230V, 825–1100 RPM | $50–$105 | $90–$185 | 295 | 400 | 545 | 0.8–1.5 | Motors | Overamp with good cap = bearing failure. Overamp with weak cap = try capacitor first. Spin blade by hand with power OFF — stiff or rough = bearing failure = replace motor.
Condenser Fan Motor — 1/4 HP | Outdoor fan. Common for 3–4T units. | 1/4 HP, 208/230V, 825–1100 RPM | $55–$115 | $95–$200 | 310 | 420 | 565 | 0.8–1.5 | Motors | If blade spins freely and motor won't start = start with capacitor. If blade stiff with power OFF = bearing failure = motor replace regardless of cap condition.
Condenser Fan Motor — 1/3 HP | Outdoor fan. Common for 4–5T units. | 1/3 HP, 208/230V, 825–1100 RPM | $60–$130 | $100–$220 | 320 | 445 | 605 | 0.8–1.5 | Motors | 5T motors take maximum abuse. Check blade pitch — bent blade from debris causes overamp even with good motor. Straighten or replace blade before condemning motor.
Universal Condenser Fan Motor | Multi-speed universal. Fits most 1.5–5T residential. Genteq/equivalent. | 1/5–1/3 HP switchable, 208/230V, reversible | $55–$120 | $95–$205 | 305 | 430 | 580 | 1.0–1.75 | Motors | Saves truck stock — one motor covers most calls. Must set correct HP, RPM, and rotation direction. Photograph OEM wiring before disconnecting.
Blower Motor — PSC 1/3 HP | Indoor air handler blower. Pre-2015 most common. | 1/3 HP, 4-speed, 208/230V, CCW | $50–$120 | $85–$195 | 325 | 445 | 590 | 1.5–2.5 | Motors | More forgiving than ECM — generic replacement works if HP/RPM/rotation match. Check blower wheel for debris while motor is out — always do this.
Blower Motor — PSC 1/2 HP | Larger PSC blower for 3–4T air handlers. | 1/2 HP, 4-speed, 208/230V, CCW | $65–$135 | $105–$220 | 365 | 480 | 635 | 1.5–2.5 | Motors | High-static duct systems stress 1/2 HP motors. Check TESP after replacement — Houston attic systems often have high static from undersized ductwork.
Blower Motor — PSC 3/4 HP | Large PSC blower for 4–5T air handlers. | 3/4 HP, 4-speed, 208/230V, CCW | $80–$155 | $130–$250 | 395 | 530 | 685 | 1.5–2.5 | Motors | Verify rotation direction before ordering — wrong direction delivers ~20% of rated airflow and mimics low charge.
Blower Motor — ECM X13 (Constant Torque) | ECM constant-torque. Mid-tier 2015+ units. Tap-selected speed. | 1/2–3/4 HP, ECM X13 module, 208/230V | $140–$320 | $220–$425 | 475 | 645 | 845 | 2.0–3.0 | Motors | X13 = constant torque. CFM varies with static pressure. Cannot use generic PSC. Must match control module. Set correct tap per unit install manual.
Blower Motor — ECM 2.3 Variable Speed | Full variable-speed ECM. Premium units (Infinity, XV, GSXV, Prestige). | 3/4–1 HP, ECM 2.3 w/ control module, 208/230V | $220–$460 | $340–$580 | 580 | 795 | 1055 | 2.0–3.5 | Motors | CRITICAL: ECM 2.3 has a separate control module — replace both together. Module stores system settings. Part number must match exactly — cannot substitute generic.
ECM Control Module Only | Replacement brain board for ECM 2.3 motor. Motor may still be good. | Genteq/Regal Rexnord ECM module | $110–$240 | $175–$325 | 365 | 495 | 655 | 0.75–1.5 | Motors | Test motor continuity first. If motor windings are good, module-only replacement saves $200–$300. Check motor leads with ohmmeter before ordering full assembly.
Inducer Motor — Draft Inducer | Gas furnace combustion blower. Failure = no heat call. | 0.5–2.5A FLA, 115V or 230V, brand-specific | $85–$280 | $140–$425 | 420 | 705 | 1105 | 1.5–3.0 | Heating | Match exact part number — not universal. High amps + no startup = check capacitor (some models have it). No rotation + correct voltage = winding failure = replace motor.
⚠ All prices are customer-facing installed (parts+labor). Wholesale=40–60% of retail. After-hours +25–50%. Emergency +50–100%. Attic premium +$25–$50.

## 3. REFRIGERANT
REFRIGERANT SERVICES (R-410A · R-22 · R-32 · R-454B) — Houston 2025–2026
PART / SERVICE | DESCRIPTION | COMMON SPECS | PART COST (Wholesale) | PART COST (Retail) | INSTALLED (Min) | INSTALLED (Typical) | INSTALLED (Max) | LABOR (Hrs) | CATEGORY | MARK'S NOTES
R-410A — Per Pound Added | Puron. Dominant 2010–2024. Existing system top-off only. | R-410A 25-lb cylinder | $8–$18 | $20–$40 | 80 | 110 | 150 | — | Refrigerant | Typical add 1–2 lbs = $160–$300. NEVER leave without finding why it was low. Document start/end pressures every time.
R-410A — Typical 1–2 lb Add | Most common refrigerant add on low-charge call. | 1–2 lb add incl. handling | N/A | $20–$40 | 160 | 225 | 300 | 0.5–1.0 | Refrigerant | Always find the leak source. UV dye + recharge is a temporary fix, not a repair.
R-410A — Full Recharge (system empty) | Full factory-spec recharge after repair. Includes evac to 300 microns. | Factory charge per nameplate | N/A | N/A | 225 | 350 | 500 | 0.75–1.25 | Refrigerant | Refrigerant cost is ON TOP of this. 3T from empty (~7 lbs) = $560–$1,050 in R-410A alone. Quote separately.
R-22 — Per Pound (Reclaim Only) | Banned production since Jan 2020. Reclaimed only. Scarce and expensive. | R-22 reclaimed, EPA 608 cert required | $50–$120 | $90–$180 | 200 | 320 | 400 | — | Refrigerant | HOUSTON NOTE: Local R-22 installed = $200–$350/lb (lower than national due to reclaim volume). If >2 lbs needed: push for full system replacement. R-22 math never wins.
R-22 — Handling Surcharge | Additional fee for R-22 cert, recovery equipment, reclaim. | EPA 608 certified tech required | N/A | N/A | 75 | 115 | 150 | 0.25–0.5 | Refrigerant | Bill separately so homeowner sees true R-22 service cost. Makes replacement conversation much easier.
R-32 — Per Pound | 2025+ new systems (Lennox Sig, Daikin). A2L mildly flammable. 15–20% higher pressure than R-410A. | R-32, A2L certified equipment REQUIRED | $20–$45 | $45–$85 | 85 | 120 | 160 | — | Refrigerant | A2L CERTIFIED EQUIPMENT ONLY. No open flames. Do NOT apply R-410A pressure targets — R-32 runs 15–20% higher. Rare in Houston field today; growing fast with 2025+ installs.
R-454B — Per Pound | EPA AIM Act mandated new residential from Jan 2025. Zeotropic blend. A2L. | R-454B (Opteon XL41/Puron Advance), A2L | $22–$50 | $48–$90 | 90 | 130 | 175 | — | Refrigerant | ZEOTROPIC: Use DEW point on suction side, BUBBLE point on liquid line. Runs 5–10% LOWER discharge than R-410A — do NOT interpret as low charge. Only ~1 year field data; verify pricing locally.
Recovery + Evacuation (300 microns) | Full system recovery, evacuation to 300 microns, pressure hold. | Recovery machine + micron gauge required | N/A | N/A | 125 | 195 | 280 | 0.5–1.0 | Refrigerant | Refrigerant cost is on top. NEVER skip evacuation — moisture = acid = compressor death. 300 microns is the standard. Pressure hold at 150 psig for 15 min minimum.
Refrigerant Leak Search | Electronic detector + UV dye injection to locate leak source. | Electronic leak detector + UV dye kit | $12–$30 | $25–$55 | 150 | 225 | 325 | 1.0–2.0 | Refrigerant | Do NOT recharge and leave. Find the leak. UV photo = homeowner evidence. Coil leak = coil replacement. Fitting leak = resolder/repair. Document everything for the report.
UV Dye Injection | UV tracer dye into refrigerant circuit. Leak glows under UV. | UV dye cartridge + UV lamp | $12–$30 | $20–$45 | 85 | 120 | 165 | 0.25–0.5 | Refrigerant | Do this on every refrigerant call. UV photo of glowing leak is the most compelling homeowner evidence for authorizing coil replacement.
Refrigerant Overcharge Correction | Recover excess refrigerant to factory weight. Measure subcooling to confirm. | Recovery machine + manifold gauges | N/A | N/A | 200 | 300 | 450 | 1.5–3.0 | Refrigerant | High discharge + high subcooling (>18°F TXV system) = overcharge. Do NOT add refrigerant — recover. Distinguish from dirty condenser via photo (dirty coil = high discharge, low subcooling).
Nitrogen Pressure Test | Pressurize refrigerant circuit with N2 before recharge. | Dry nitrogen, 150–200 psig | $8–$20 | $15–$35 | 85 | 130 | 185 | 0.5–0.75 | Refrigerant | Required after any refrigerant-side repair. 15-min hold at 150 psig. Zero drop = tight system. Any drop = find the leak before charging.
Lineset Flush (after burnout) | Full lineset flush with refrigerant flush solvent after compressor burnout. | Flush solvent + flush kit | $35–$85 | $55–$140 | 250 | 385 | 575 | 1.5–3.0 | Refrigerant | MANDATORY after compressor burnout — acid contamination in lineset will kill the new compressor within a season. Skip this step and you'll be back in 6 months.
Lineset Replacement (per linear ft) | Replace copper lineset. Includes labor + materials + flaring/brazing. | 3/8" suction + 7/8" or 1-1/8" liquid line, per ft | N/A | N/A | 18 | 28 | 40 | 0.25–0.4 | Refrigerant | Per linear foot installed. Typical Houston residential lineset = 15–40 ft. Minimum trip charge usually applies. Required when upgrading from R-22 to R-410A system.
⚠ All prices = customer-facing installed (parts+labor). Wholesale=40–60% of retail. After-hours +25–50%. Emergency +50–100%. Attic premium +$25–$50.

## 4. REFRIG CONTROLS
REFRIGERANT CONTROLS (TXV · Piston · Reversing Valve · EEV · Defrost) — Houston 2025–2026
PART / SERVICE | DESCRIPTION | COMMON SPECS | PART COST (Wholesale) | PART COST (Retail) | INSTALLED (Min) | INSTALLED (Typical) | INSTALLED (Max) | LABOR (Hrs) | CATEGORY | MARK'S NOTES
TXV Valve — 2 Ton | Thermostatic expansion valve at indoor coil. Requires refrigerant recovery. | R-410A TXV, 2T, indoor coil mount | $45–$110 | $85–$195 | 375 | 490 | 650 | 2.5–4.5 | Refrig Controls | Requires full recovery + replace + evac + recharge labor. Refrigerant cost is on top. Confirm TXV failure with oscillating suction pressure over 30–60 sec cycles (hunting).
TXV Valve — 2.5–3 Ton | TXV for 2.5T or 3T system. Match tonnage and refrigerant type exactly. | R-410A TXV, 2.5–3T | $55–$130 | $95–$215 | 400 | 530 | 695 | 2.5–4.5 | Refrig Controls | TXV hunting in Houston is significantly more common than other climates due to 70°F+ dew points destabilizing TXV control. Do NOT recharge a hunting system — charge is not the issue.
TXV Valve — 4–5 Ton | TXV for 4T or 5T system. Larger valve body, higher capacity. | R-410A TXV, 4–5T | $70–$160 | $115–$250 | 430 | 570 | 740 | 2.5–4.5 | Refrig Controls | If TXV bulb clamp is loose or poorly insulated, reseat and insulate first before condemning valve. Saves $500+ if that fixes the hunting.
Fixed Orifice / Piston — 1.5T | Fixed bore metering device. 1.5T = 0.049" bore (R-410A). | R-410A bore 0.049" (49) | $8–$18 | $18–$40 | 275 | 350 | 480 | 2.0–3.5 | Refrig Controls | WARNING: R-22 pistons are LARGER than R-410A. Installing wrong refrigerant piston = severe charge issue. Always verify refrigerant type before cross-referencing bore.
Fixed Orifice / Piston — 2T | 2T = 0.053" bore (R-410A). | R-410A bore 0.053" (53) | $8–$18 | $18–$40 | 275 | 350 | 480 | 2.0–3.5 | Refrig Controls | Most common piston mismatch in Houston: R-22 to R-410A system swap where original R-22 piston was left in place. Too large bore = high suction, low superheat, flooding.
Fixed Orifice / Piston — 2.5T | 2.5T = 0.059" bore (R-410A). | R-410A bore 0.059" (59) | $8–$18 | $18–$40 | 280 | 355 | 490 | 2.0–3.5 | Refrig Controls | Bore measurement tool required. Confirm actual bore vs nameplate tonnage. 2+ sizes off = mismatch.
Fixed Orifice / Piston — 3T | 3T = 0.068" bore (R-410A). Most common residential tonnage. | R-410A bore 0.068" (68) | $8–$20 | $18–$42 | 280 | 360 | 495 | 2.0–3.5 | Refrig Controls | After any system swap or coil replacement, ALWAYS verify the correct piston was installed. Technician error here causes callback immediately on first run.
Fixed Orifice / Piston — 3.5–4T | 3.5T = 0.074", 4T = 0.080" bore (R-410A). | R-410A bore 0.074" or 0.080" | $9–$22 | $20–$46 | 285 | 365 | 500 | 2.0–3.5 | Refrig Controls | 4T piston (0.080") is different from 3.5T (0.074"). Do not substitute. Too small = high superheat, starved coil.
Fixed Orifice / Piston — 5T | 5T = 0.090" bore (R-410A). | R-410A bore 0.090" (90) | $9–$22 | $20–$46 | 285 | 365 | 500 | 2.0–3.5 | Refrig Controls | 5T systems: verify suction line size too. Wrong piston + undersized suction line = double restriction.
EEV — Electronic Expansion Valve | EEV for variable-speed/inverter systems (Infinity, XV, GSXV, Daikin Fit). Controlled by unit board. | Brand-specific EEV, R-410A or R-454B | $120–$350 | $220–$520 | 520 | 780 | 1050 | 3.0–5.0 | Refrig Controls | EEV failure on inverter system often shows as erratic superheat with unit throwing refrigerant fault codes. Usually requires board communication check too. Brand-specific — no substitutes.
Reversing Valve — Standard | 4-way reversing valve for heat pump. Controls heat/cool mode reversal. | Brand-compatible, R-410A | $75–$200 | $120–$285 | 450 | 625 | 850 | 3.5–5.5 | Refrig Controls | Requires full refrigerant handling. Confirm stuck direction (stuck in cooling = can cool but not heat; stuck in heating = opposite). Rarely fails in Houston due to low heating demand.
Reversing Valve — Premium Brand | Reversing valve for Carrier Infinity, Trane XV, Lennox XC — often OEM only. | OEM brand-specific, R-410A | $120–$280 | $185–$380 | 580 | 780 | 1050 | 3.5–5.5 | Refrig Controls | Premium system reversing valves often require OEM sourcing through brand distributor (Carrier Enterprise, Trane Supply). Lead time can be 2–5 business days. Warn homeowner upfront.
Defrost Control Board | Heat pump defrost board. Controls defrost cycle initiation and termination. | Brand-specific defrost board | $60–$180 | $100–$300 | 300 | 480 | 650 | 0.75–1.5 | Controls | Defrost fault in Houston is rare — most calls are Nov–Feb cold snaps. Stuck in defrost >15 min = defrost board or sensor. Never defrosts + iced outdoor coil = board or sensor.
Defrost Sensor / Thermostat | Temperature sensor that tells defrost board when to initiate/terminate defrost. | Clip-on coil thermostat, brand-specific | $15–$45 | $28–$75 | 150 | 225 | 340 | 0.5–0.75 | Controls | Cheap part. If defrost board checks out OK, replace sensor first — it's $28 vs $300. Test by bypassing sensor with jumper — if system defrosts normally, sensor is the fault.
⚠ All prices = customer-facing installed (parts+labor). Wholesale=40–60% of retail. After-hours +25–50%. Emergency +50–100%. Attic premium +$25–$50.

## 5. COILS
COILS (Evaporator · Condenser · Cleaning) — Houston Installed 2025–2026
PART / SERVICE | DESCRIPTION | COMMON SPECS | PART COST (Wholesale) | PART COST (Retail) | INSTALLED (Min) | INSTALLED (Typical) | INSTALLED (Max) | LABOR (Hrs) | CATEGORY | MARK'S NOTES
Evaporator Coil — 2T (R-410A) | A-coil or slab coil. Indoor air handler. Must match system tonnage + metering. | R-410A, 2T, TXV or piston match | $280–$480 | $450–$780 | 900 | 1200 | 1550 | 3.5–5.5 | Coils | Must match tonnage, refrigerant, and metering type. Wrong match = chronic mischarge complaints. Always verify before ordering.
Evaporator Coil — 2.5T (R-410A) | A-coil, 2.5T. Most common Houston residential coil size. | R-410A, 2.5T | $310–$520 | $490–$840 | 950 | 1280 | 1650 | 3.5–5.5 | Coils | 2.5T is the single most common coil in Houston residential. Keep 2.5T TXV and piston versions in supplier relationship for quick pull.
Evaporator Coil — 3T (R-410A) | A-coil, 3T. Very common. Most common Houston new construction size. | R-410A, 3T | $330–$560 | $530–$880 | 975 | 1320 | 1700 | 3.5–5.5 | Coils | Formicary corrosion most common on copper-fin evap coils. Check for green/white powder on coil face — sign of pinhole leaks from VOCs. Always UV dye to confirm active leak before quoting coil.
Evaporator Coil — 3.5T (R-410A) | A-coil, 3.5T. | R-410A, 3.5T | $370–$600 | $570–$930 | 1025 | 1380 | 1780 | 4.0–6.0 | Coils | Less common tonnage but found in 1,800–2,200 sq ft homes. Verify exactly with nameplate — 3T vs 3.5T coil is NOT interchangeable.
Evaporator Coil — 4T (R-410A) | A-coil, 4T. Used in 2,000–2,800 sq ft Houston homes. | R-410A, 4T | $420–$720 | $650–$1100 | 1300 | 1720 | 2250 | 4.5–6.5 | Coils | Access is more labor-intensive on attic systems. Houston attic premium applies. Weigh repair vs full system — if unit is 10+ years old, full replace often wins.
Evaporator Coil — 5T (R-410A) | A-coil, 5T. Large homes, 2,800+ sq ft. | R-410A, 5T | $480–$840 | $720–$1200 | 1400 | 1850 | 2450 | 4.5–6.5 | Coils | 5T coils in attic installations are physically large and heavy. Two-person job. Bill labor premium. If ductwork access is poor, add another $200–$400 to estimate.
Evaporator Coil — R-22 (2–3T) | Legacy R-22 coil for pre-2010 units. Increasingly hard to source. | R-22, 2–3T, piston or TXV | $350–$650 | $550–$950 | 1050 | 1450 | 1900 | 3.5–5.5 | Coils | Availability declining rapidly. If R-22 coil leaks, this is the strongest trigger for full system replacement conversation. New R-22 coil + future R-22 charges = bad economics.
Condenser Coil Replacement (2–3T) | Replacement outdoor condenser coil. OEM or aftermarket. Requires refrigerant handling. | R-410A, 2–3T, OEM or aftermarket | $280–$580 | $450–$900 | 850 | 1300 | 1750 | 2.5–4.5 | Coils | Condenser coil leaks less common than evap. Usually from physical damage (hail, lawn equipment) or severe corrosion. Get photo — hail damage may be covered by homeowner insurance.
Condenser Coil Replacement (4–5T) | Large condenser coil. More refrigerant, more labor. | R-410A, 4–5T | $400–$750 | $620–$1100 | 1100 | 1650 | 2250 | 3.0–5.0 | Coils | Insurance claim potential for hail damage. Take clear photos before quote. OEM vs aftermarket price difference can be $300–$500 — discuss with homeowner.
Condenser Coil Cleaning (Outdoor) | Chemical coil cleaner + rinse. Removes dirt, grass, fin blockage. | Coil cleaner spray + water rinse | $15–$40 | $20–$55 | 145 | 195 | 285 | 0.75–1.5 | Maintenance | Top Houston upsell on service calls. High discharge pressure + high subcooling (without being overcharge) = dirty condenser. YOLO photo confirms. Restores 5–8% efficiency.
Evaporator Coil Cleaning (Indoor) | No-rinse evap coil cleaner. More labor due to air handler access. | No-rinse coil cleaner spray | $18–$45 | $25–$60 | 185 | 265 | 375 | 1.25–2.0 | Maintenance | Delta-T below 14°F with correct charge and clean filter = dirty evap coil. Access through air handler panel. No-rinse formula drips into drain pan — protect wiring below.
Formicary Corrosion — Coil Replacement | Pinhole leaks from formic acid VOCs. Green/white powder on coil face. | Evaporator coil replacement (see coil sizes above) | N/A | N/A | 950 | 1400 | 2050 | 3.5–6.0 | Coils | UV dye confirms active leak. Green powder on coil face = formicary — coil replacement required, cannot be patched. Source: VOCs from cleaning products, plywood off-gassing. Common in new Houston builds.
⚠ All prices = customer-facing installed (parts+labor). Wholesale=40–60% of retail. After-hours +25–50%. Emergency +50–100%. Attic premium +$25–$50.

## 6. COMPRESSORS
COMPRESSORS (1.5T–5T, Single-Stage, Two-Stage, Inverter) — Houston 2025–2026
PART / SERVICE | DESCRIPTION | SPECS / NOTES | PART COST (Wholesale) | PART COST (Retail) | INSTALLED (Min) | INSTALLED (Typical) | INSTALLED (Max) | LABOR (Hrs) | CATEGORY | MARK'S NOTES
Compressor — 1.5 Ton | Single-stage scroll or reciprocating. Common in condos, small additions. | 208/230V, 18,000 BTU, RLA 6–8.5A | $200–$340 | $320–$500 | 800 | 1050 | 1350 | 3.0–5.0 | Compressor | Common in Houston condos and townhomes. If unit is R-22 AND compressor fails: strong replacement case — R-22 + compressor ≈ 60–80% of new system cost. Warranty labor only: $380–$600.
Compressor — 2 Ton | Single or two-stage. Common in smaller Houston homes/apartments. | 208/230V, 24,000 BTU, RLA 8–11A | $280–$480 | $420–$680 | 950 | 1200 | 1550 | 3.5–5.5 | Compressor | If under warranty (10-yr parts): labor only $450–$700. Always test capacitor and contactor before condemning compressor — over-amping from bad cap is common diagnosis mistake.
Compressor — 2.5 Ton | Most common Houston residential tonnage. Single or two-stage. | 208/230V, 30,000 BTU, RLA 10–13.5A | $320–$520 | $480–$740 | 1050 | 1300 | 1700 | 4.0–6.0 | Compressor | Verify compressor failure with: locked rotor (LRA), grounded windings (ohm to ground), or open windings. Do NOT condemn based on amps alone without confirming pressure readings.
Compressor — 3 Ton | Standard builder-grade Houston home size. Very high service volume. | 208/230V, 36,000 BTU, RLA 12–16A | $350–$550 | $520–$780 | 1100 | 1400 | 1750 | 4.0–6.0 | Compressor | Highest service volume compressor in Houston market. If 8+ years old: advise replacement vs repair. $1,400 compressor on an 8-year-old system is a hard sell vs $5,500 new system.
Compressor — 3.5 Ton | Used in mid-large Houston homes (1,800–2,400 sq ft typical). | 208/230V, 42,000 BTU, RLA 14–18.5A | $380–$600 | $560–$840 | 1200 | 1500 | 1950 | 4.0–6.0 | Compressor | Less commonly stocked — may require 1–2 day lead time. Confirm with supplier before quoting homeowner timeline.
Compressor — 4 Ton | Larger homes. High humidity load in Houston. | 208/230V, 48,000 BTU, RLA 17–21.5A | $420–$680 | $620–$950 | 1300 | 1650 | 2100 | 4.5–6.5 | Compressor | 4T compressor replacement is at the tipping point where full system replacement is often better economics. Always present both options with TCO comparison.
Compressor — 5 Ton | Largest residential single-phase compressor. 2,800+ sq ft. | 208/230V, 60,000 BTU, RLA 20–25.5A | $520–$850 | $750–$1150 | 1550 | 2000 | 2500 | 5.0–7.0 | Compressor | At $2,000 installed, full system replacement is almost always the better recommendation for 7+ year units. Present 5T replacement at $7,000–$9,000 vs repair + risk of next failure.
Compressor — Inverter/Variable Speed (1.5–3T) | Variable-speed inverter compressor. Carrier Infinity, Trane XV, Lennox XC, Goodman GSXV, Daikin Fit. | VFD-controlled, 208/230V, VFD nameplate amps | $680–$1400 | $1100–$2200 | 1800 | 2600 | 3800 | 5.0–8.0 | Compressor | INVERTER RULE: Do NOT compare amps to standard RLA table. Compare to NAMEPLATE VFD amps. Hard-start kit is NOT compatible — will damage VFD. At partial load: 30–60% of nameplate amps is normal.
Compressor — Inverter/Variable Speed (3.5–5T) | Large variable-speed inverter compressor. | VFD-controlled, 208/230V, large frame | $950–$1900 | $1500–$2800 | 2500 | 3500 | 5200 | 5.0–8.0 | Compressor | Expensive part + expensive labor. At this price point, full premium system replacement ($12,000–$18,000) should always be on the table. System still in warranty: contact brand tech support before replacing.
Compressor — R-22 (2–3T, Reconditioned) | Reconditioned R-22 compressor for pre-2010 units. New R-22 compressors not manufactured. | R-22, 2–3T, reconditioned/rebuildable | $180–$380 | $290–$580 | 850 | 1200 | 1650 | 4.0–6.0 | Compressor | R-22 compressor failure = strongest replacement trigger. Between R-22 refrigerant + compressor cost, replacement economics are almost always better. Present both options with clear math.
⚠ All prices = customer-facing installed (parts+labor). Wholesale=40–60% of retail. Attic access in Houston summer = additional labor premium.

## 7. HEATING PARTS
HEATING PARTS (Gas Furnace — Ignitor · Flame Sensor · Gas Valve · Heat Exchanger) — Houston 2025–2026
PART / SERVICE | DESCRIPTION | SPECS / NOTES | PART COST (Wholesale) | PART COST (Retail) | INSTALLED (Min) | INSTALLED (Typical) | INSTALLED (Max) | LABOR (Hrs) | CATEGORY | MARK'S NOTES
Hot Surface Ignitor (HSI) | Silicon carbide or silicon nitride ignitor. Gas furnace only. Very fragile. | Silicon carbide 40–90Ω, or silicon nitride | $12–$45 | $22–$70 | 165 | 235 | 325 | 0.5–0.75 | Heating | Handle with clean gloves — skin oil causes hot spots and premature failure. Measure resistance: 40–90Ω = good. Open circuit = failed. Carrier: 62-24084-88. Check model spec.
Flame Sensor Rod | Stainless steel sensing rod. Cleanable with steel wool before replacing. | Stainless rod, 1/4" spade terminal | $5–$18 | $10–$30 | 120 | 165 | 235 | 0.4–0.65 | Heating | Check microamp reading first (normal = 2–10 µA). Below 1 µA = clean with fine steel wool. If still below 1 µA after cleaning = replace. Furnace lights then shuts off in 5–10 sec = flame sensor 90% of the time.
Gas Valve | 24V electric gas valve. Controls pilot and main burner gas flow. | 24V, natural gas or LP, brand-specific | $75–$180 | $120–$280 | 375 | 545 | 750 | 1.0–2.0 | Heating | Verify 24V is present at valve before condemning. No 24V = control board or wiring issue. 24V present but no gas = valve failed. Gas smell with system off = valve leaking by — safety shutoff immediately.
Gas Valve — LP/Propane Conversion | LP orifice kit or LP-rated gas valve for propane-fueled systems. | LP conversion kit or LP gas valve | $35–$90 | $60–$150 | 195 | 310 | 450 | 0.75–1.5 | Heating | Propane manifold pressure = 11" WC (vs 3.5" WC natural gas). MUST set correctly or risk incomplete combustion or rollout. Tag system clearly after LP conversion.
Pressure Switch (Inducer Draft) | Safety switch verifying inducer motor is creating draft before gas lights. | 0.5–2.0" WC switch, brand-specific | $18–$55 | $35–$90 | 150 | 230 | 345 | 0.5–1.0 | Heating | Test with manometer — confirm switch is getting correct negative pressure from inducer. Blocked condensate tubing to switch is #1 cause of pressure switch codes. Clear the tubing before condemning switch.
High Limit Switch | Temperature safety switch. Trips at 150–200°F to prevent heat exchanger damage. | 150–200°F trip temp, auto or manual reset | $12–$40 | $22–$70 | 145 | 215 | 310 | 0.4–0.75 | Heating | If high limit trips repeatedly: find root cause first — dirty filter, blocked ductwork, failed blower, wrong speed tap. Repeated tripping with no airflow cause = cracked heat exchanger investigation.
Rollout Switch | Manual-reset safety. Trips if flame rolls out of combustion chamber. | 250–350°F trip temp, manual reset | $10–$35 | $18–$60 | 135 | 200 | 295 | 0.4–0.75 | Heating | Rollout = gas pressure too high OR cracked heat exchanger. NEVER reset and leave without finding cause. CO risk is real — homeowner safety issue.
Heat Exchanger — Crack Inspection | CO measurement + visual inspection of heat exchanger for cracks. | CO analyzer, mirror, camera inspection | N/A | N/A | 145 | 225 | 350 | 1.0–2.0 | Heating | CO above 100 ppm air-free in flue gas = investigate heat exchanger. Above 200 ppm = shut furnace down immediately. Cracked exchanger = CO entering living space = life safety.
Heat Exchanger — Replacement (Mid-Efficiency) | Full heat exchanger replacement. 80% AFUE furnaces. | 80% AFUE, natural gas, brand-specific | $380–$750 | $600–$1100 | 1050 | 1750 | 2600 | 4.0–7.0 | Heating | In most Houston cases: if heat exchanger is cracked, recommend full furnace replacement. New heat exchanger cost approaches 50–70% of a new 80% furnace. Present both options.
Heat Exchanger — Replacement (High-Efficiency) | Full heat exchanger for 90–96% AFUE condensing furnace. | 90–96% AFUE, stainless secondary HX | $500–$950 | $800–$1500 | 1300 | 2200 | 3500 | 5.0–8.0 | Heating | High-efficiency HX replacement almost always triggers replacement recommendation — parts cost alone can exceed 60% of new furnace. Homeowner insurance sometimes covers if CO event documented.
Furnace Control Board | Main furnace control board. Manages ignition sequence, blower, limits. | Brand-specific, 24V signal board | $65–$220 | $105–$350 | 350 | 530 | 720 | 0.75–1.5 | Heating | LED fault code from board narrows diagnosis dramatically. Always decode the flash pattern before condemning board. Document code for homeowner report.
Furnace Blower Capacitor | Run capacitor for furnace blower motor on PSC-type air handlers. | 5–15 MFD, 370V/440V | $8–$22 | $18–$45 | 100 | 155 | 230 | 0.3–0.5 | Heating | Quick and cheap fix. If blower hums but won't spin — capacitor first. Verify correct MFD and voltage rating on nameplate.
Condensing Furnace Drain System | Condensate drain, trap, and pump for 90%+ efficiency furnace. | PVC drain, condensate trap, pump if needed | $20–$65 | $35–$110 | 175 | 295 | 445 | 0.75–1.5 | Heating | Condensing furnaces produce acidic condensate (pH 3–4). Drain must run to utility sink or pump to exterior — not to main AC drain pan. Plugged condensate drain = pressure switch trip.
CO Detector / Alarm Install | Residential CO alarm installation near furnace. Code requirement. | UL-listed CO detector, hardwired or plug-in | $20–$55 | $35–$80 | 90 | 145 | 215 | 0.25–0.5 | Heating | Required by Houston code within 15 ft of any fuel-burning appliance. Recommend on every furnace call — $145 install is cheap insurance vs liability from undocumented CO concern.
⚠ All prices = customer-facing installed (parts+labor). Wholesale=40–60% of retail. Attic access in Houston summer = additional labor premium.

## 8. MAINTENANCE
MAINTENANCE, CLEANING & SERVICE — Houston Installed 2025–2026
PART / SERVICE | DESCRIPTION | SPECS / NOTES | PART COST (Wholesale) | PART COST (Retail) | INSTALLED (Min) | INSTALLED (Typical) | INSTALLED (Max) | LABOR (Hrs) | CATEGORY | MARK'S NOTES
Air Filter — 1" Standard (MERV 8) | Standard pleated 1-inch filter. Most common Houston residential. | 14x20, 16x20, 16x25, 20x25, 20x20 | $10–$28 | $15–$40 | 18 | 30 | 45 | 0.15–0.25 | Maintenance | Recommend quarterly changes in Houston due to high humidity and mold potential. Upsell to MERV 11 if customer has pets or allergies.
Air Filter — 1" MERV 11 | Higher efficiency pleated 1-inch filter. Better particle capture. | MERV 11, standard sizes | $14–$35 | $20–$50 | 22 | 38 | 55 | 0.15–0.25 | Maintenance | MERV 13+ on standard residential systems = airflow restriction risk. MERV 11 is the sweet spot for Houston residential — better filtration without excessive static.
Air Filter — 4–5" Media (MERV 11–13) | High-capacity media filter. Lasts 6–12 months. Requires media cabinet. | MERV 11–13, Honeywell/Aprilaire/Carrier | $28–$80 | $45–$120 | 55 | 80 | 125 | 0.15–0.25 | Maintenance | Strongly recommend media cabinet + 5" filter on initial install. Monthly 1" filter cost over 10 years vs annual media cost = comparable, but media is better filtration.
Condensate Drain Flush — Chemical | Chemical flush of drain line. Includes flush tablet left in pan. | Drain flush tablet/solution + CO2 flush gun | $8–$25 | $12–$35 | 120 | 165 | 225 | 0.5–0.75 | Maintenance | #1 Houston call by volume. High humidity + organic matter = algae bloom in drain pan weekly in summer. Always leave a pan tablet. Recommend quarterly flush service contract.
Drain Pan Full Clean-Out | Deep clean of drain pan with algaecide treatment + line flush. | Algaecide, pan cleaner, CO2 gun | $12–$35 | $18–$50 | 145 | 185 | 250 | 0.75–1.25 | Maintenance | If pan has standing water or visible algae growth — full clean-out, not just a flush. Secondary float switch check: if tripped, verify pan drain is completely clear.
Condensate Pan Treatment Tablet | Slow-release pan tablet. Prevents algae regrowth. Add at every drain service. | Pan tablet, 3-month or 6-month formula | $8–$20 | $10–$25 | 18 | 25 | 38 | 0.1–0.1 | Maintenance | Cheap insurance. Leave one in the pan at the end of every single drain service call. Cost: $2. Callback prevention: very high. Never skip this step.
Condenser Coil Cleaning (Outdoor) | Chemical coil cleaner + rinse. Removes dirt, grass, fin blockage. | Coil cleaning spray, garden hose rinse | $15–$40 | $20–$55 | 145 | 195 | 285 | 0.75–1.5 | Maintenance | High discharge pressure with normal charge = dirty condenser first. YOLO photo confirms. Restores 5–8% efficiency. Best spring upsell — sell with tune-up package.
Evaporator Coil Cleaning (Indoor) | No-rinse evap cleaner. More labor due to air handler access. | Nu-Brite or equivalent no-rinse spray | $18–$45 | $25–$60 | 185 | 265 | 375 | 1.25–2.0 | Maintenance | Delta-T below 14°F with correct charge and clean filter = dirty evap. Foam drips into drain pan — protect wiring. Always flush drain after evap cleaning.
UV Germicidal Light — Single Lamp | UV-C light installed in air handler. Kills mold and bacteria on coil. | UV-C single lamp, 115V, 12" or 17" | $55–$120 | $90–$195 | 250 | 355 | 520 | 0.75–1.25 | Maintenance | Houston = high mold risk from 74% average RH. Great upsell on any system with visible coil mold. UV light also keeps drain pan cleaner. Lamp replacement every 12–18 months: $80–$150.
UV Germicidal Light — Dual Lamp | Dual UV-C lamp system. Coil + air stream treatment. | Dual UV-C, 115V | $95–$195 | $150–$325 | 380 | 550 | 750 | 0.75–1.5 | Maintenance | Stronger than single lamp. Treat both coil and return air stream. Best option for customers with mold allergies or visible coil contamination. Sell annual lamp replacement contract.
UV Lamp Replacement | Annual UV lamp replacement. Output degrades even if still illuminated. | UV-C replacement lamp, 12" or 17" | $25–$65 | $45–$110 | 80 | 130 | 195 | 0.25–0.5 | Maintenance | Lamps lose 50%+ output after 12–18 months even if still glowing. Sell annual replacement contract at install.
Float Switch — Primary | Inline float switch in main condensate drain line. Kills system on high water. | SS-1 or equivalent inline float | $12–$30 | $22–$55 | 145 | 195 | 290 | 0.5–0.75 | Maintenance | Houston code requires float switch on air handler installations. Primary float shuts down air handler before pan overflow. Cheap part — replace if stuck or corroded on service visit.
Float Switch — Secondary (Pan) | Secondary float switch in emergency drain pan. Backup water detection. | Pan-mount float switch | $15–$35 | $25–$65 | 155 | 215 | 320 | 0.5–0.75 | Maintenance | Secondary float protects against ceiling water damage if primary fails. STRONGLY recommend if air handler is attic-mounted over finished ceiling. Houston water damage from AC drain = common homeowner nightmare.
Annual Service Tune-Up (Full System) | Annual PM: inspect, clean, test all electrical, check refrigerant, flush drain. | Full system inspection + drain flush + pan tablet | N/A | N/A | 120 | 155 | 200 | 1.0–1.5 | Maintenance | Base tune-up price — individual findings added as separate line items. Typical upsells: filter, capacitor pre-replace, coil cleaning, drain flush. Good spring service generates $400–$800 per call.
Service Call / Diagnostic Fee | Standard diagnostic fee. Many Houston companies waive if repair booked. | Includes travel + first 30–60 min | N/A | N/A | 85 | 125 | 175 | 0.5–1.0 | Service | Document everything at diagnostic — photos, measurements, readings. This is what feeds the homeowner report and authorizes the repair. Never leave without a written finding.
After-Hours Service Premium | Additional charge for evening/weekend emergency calls. | 25–50% surcharge on labor | N/A | N/A | 50 | 90 | 150 | — | Service | Standard Houston practice. Communicate clearly upfront. Many customers will wait until morning once they understand cost difference.
⚠ All prices = customer-facing installed (parts+labor). Wholesale=40–60% of retail. Attic access in Houston summer = additional labor premium.

## 9. CONTROLS
CONTROLS & THERMOSTATS — Houston Installed 2025–2026
PART / SERVICE | DESCRIPTION | SPECS / NOTES | PART COST (Wholesale) | PART COST (Retail) | INSTALLED (Min) | INSTALLED (Typical) | INSTALLED (Max) | LABOR (Hrs) | CATEGORY | MARK'S NOTES
Control Board — Outdoor Unit | Main control/defrost board in outdoor unit. Brand-specific. | Brand-specific PCB, varies by model | $60–$220 | $100–$340 | 350 | 500 | 700 | 0.75–1.5 | Controls | ALWAYS decode the LED fault code before condemning board. Photo the board. Expensive and non-returnable if incorrectly diagnosed.
Control Board — Indoor/Air Handler | Air handler control board. Manages blower, heat strips, fault codes. | Brand-specific AH control board | $65–$230 | $105–$350 | 355 | 510 | 710 | 0.75–1.5 | Controls | Check board fuse first — 3A or 5A mini fuse blows when thermostat wire shorts. $2 fuse vs $510 board. Never skip the fuse check.
Infinity System Board (Carrier/Bryant) | Carrier Infinity / Bryant Evolution variable-speed system board. | Infinity control board, brand-specific | $120–$380 | $195–$580 | 550 | 750 | 1050 | 1.0–2.0 | Controls | All components talk on 2-wire bus. Board failure shows as comm errors on thermostat. Check wiring connections first.
ComfortLink Board (Trane XV) | Trane XV21i/XV20i communicating system control board. | Trane ComfortLink board, model-specific | $120–$390 | $200–$590 | 560 | 770 | 1070 | 1.0–2.0 | Controls | Check comm wiring + 24V to all components before blaming board.
Communicating Board — Inverter Systems | Board for Lennox XC/SL, Goodman GSXV, Rheem Prestige variable-speed. | Brand-specific VFD control board | $130–$420 | $210–$620 | 580 | 800 | 1120 | 1.0–2.0 | Controls | Inverter board failure often presents as compressor fault with no obvious cause. Check error codes and VFD input voltage.
Thermostat — Basic Programmable | Non-smart 7-day programmable. Replaces failed basic stat. | Honeywell T6 Pro, White-Rodgers, etc. | $25–$65 | $45–$110 | 130 | 185 | 275 | 0.5–1.0 | Controls | Thermostat is rarely the failure on no-cool calls. Verify 24V at stat terminals before condemning.
Thermostat — Smart WiFi | Smart WiFi thermostat. Ecobee, Honeywell T9, Google Nest. | Ecobee SmartStat, Honeywell T9, Nest | $130–$250 | $175–$325 | 275 | 385 | 520 | 0.75–1.25 | Controls | Great upsell on any service call. Ecobee most contractor-friendly — supports add-a-wire kit. Remote monitoring catches failures early.
Thermostat — Communicating System | Carrier Infinity, Trane ComfortLink, Lennox iComfort S30. Must match system. | System-specific communicating thermostat | $220–$480 | $320–$650 | 450 | 650 | 900 | 0.75–1.25 | Controls | Non-communicating stat CANNOT replace Infinity/XV communicating stat — system drops to basic mode. Source through brand distributor.
Thermostat — Dual Fuel Capable | For heat pump + gas furnace (dual fuel) systems. | Ecobee Premium, Honeywell Prestige IAQ | $160–$320 | $230–$450 | 375 | 545 | 750 | 0.75–1.25 | Controls | Must support O/B reversing valve wire AND gas furnace aux input. Set switchover temp (Houston typical: 38–42°F).
Thermostat C-Wire Adapter | Add C-wire to systems without dedicated C terminal. | Venstar Add-a-Wire or equivalent | $12–$30 | $20–$55 | 75 | 120 | 185 | 0.35–0.6 | Controls | Smart thermostats need 24V common. Add-a-wire adapter is clean solution vs running new thermostat wire through attic.
Thermostat Wire — Per Run | Replace damaged thermostat wire. 5-wire or 8-wire. | 18/5 or 18/8, per installed run | N/A | N/A | 165 | 280 | 450 | 1.5–3.0 | Controls | Rodent damage to thermostat wire is common in Houston attics. Attic runs add labor premium. Range covers typical Houston installation, not per-foot.
⚠ All prices = customer-facing installed (parts+labor). Wholesale=40–60% of retail.

## 10. MINI-SPLITS
MINI-SPLIT PARTS & SERVICE (Mitsubishi · Daikin · LG · Samsung · Gree · Pioneer · MrCool · Bosch) — Houston 2025–2026
PART / SERVICE | DESCRIPTION | SPECS / NOTES | PART COST (Wholesale) | PART COST (Retail) | INSTALLED (Min) | INSTALLED (Typical) | INSTALLED (Max) | LABOR (Hrs) | CATEGORY | MARK'S NOTES
Mini-Split Inverter Board (Outdoor) | Main inverter/VFD board. Most expensive common mini-split repair. | Brand-specific: Mitsubishi, Daikin, LG, Samsung, Gree, Pioneer, MrCool, Bosch | $150–$420 | $250–$620 | 550 | 775 | 1050 | 2.0–3.5 | Mini-Split | Cannot substitute generic — must match exact model board. Mitsubishi + Daikin OEM through distributors. Gree/Pioneer/MrCool: HVACDirect.com.
Mini-Split PCB — Indoor Unit | Control board in wall-mount indoor unit. | Brand-specific indoor PCB | $80–$220 | $135–$380 | 380 | 550 | 750 | 1.5–2.5 | Mini-Split | Check communication wiring between indoor and outdoor before condemning board (LG CH05, Mitsubishi P8).
Mini-Split PCB — Outdoor Unit | Control board in outdoor unit (separate from inverter on some brands). | Brand-specific outdoor PCB | $90–$250 | $145–$420 | 395 | 580 | 800 | 1.5–2.5 | Mini-Split | On Mitsubishi MXZ multi-zone: outdoor board failure affects ALL indoor units simultaneously.
Mini-Split EEV | EEV metering device. All mini-splits use EEV. | Brand-specific EEV, R-410A | $65–$180 | $110–$320 | 350 | 520 | 720 | 2.0–3.5 | Mini-Split | EEV failure: high superheat or flooding, unit cycling on protection mode. Requires refrigerant recovery.
Mini-Split Fan Motor — Indoor | Cross-flow fan motor for indoor wall-mount unit. | Brand-specific, 12–30W DC | $45–$130 | $80–$250 | 300 | 430 | 600 | 1.5–2.5 | Mini-Split | Must match exact model for blade attachment compatibility.
Mini-Split Fan Motor — Outdoor | Propeller fan motor for outdoor condenser unit. | Brand-specific, DC brushless | $55–$150 | $90–$280 | 320 | 460 | 640 | 1.0–2.0 | Mini-Split | DC brushless — cannot substitute AC fan motor. LG CH21 (high pressure/fan fault), Mitsubishi P5.
Mini-Split Thermistor / Sensor | Temperature sensor. Multiple per unit — discharge, ambient, coil. | Brand-specific thermistor set | $15–$45 | $28–$80 | 200 | 320 | 450 | 0.75–1.5 | Mini-Split | Cheap part. Thermistor failure shows as refrigerant protection codes. Check with ohmmeter vs temp chart before ordering refrigerant.
Mini-Split Refrigerant Service — R-410A | Leak search + recovery + recharge. Refrigerant cost on top. | R-410A, manifold gauges, scale | N/A | N/A | 380 | 545 | 750 | 2.0–3.5 | Mini-Split | Mini-splits have smaller factory charge (1–4 lbs). Lineset length affects required charge — add per manufacturer spec.
Mini-Split Drain Pump | Condensate pump where gravity drain is not possible. | Mini-split condensate pump, 115V | $35–$85 | $60–$145 | 215 | 320 | 460 | 0.75–1.5 | Mini-Split | Drain pump failure = water from indoor unit. Replace pump + check drain line on same visit.
Mini-Split Deep Clean — Indoor Unit | Full disassembly clean: fan, coil, blower wheel. | No-rinse coil cleaner + pressure wash | N/A | N/A | 185 | 285 | 425 | 1.25–2.0 | Mini-Split | Annual in Houston. Mold smell from indoor unit = immediate revenue opportunity. Houston 74% RH = fastest mold growth of any major US city.
Mini-Split Diagnostic Service Call | Diagnostic for mini-split. Slightly higher than central due to specialty. | All brands, error code + gauges | N/A | N/A | 95 | 145 | 195 | 0.5–1.0 | Mini-Split | Read error code from indoor display + outdoor LED. Reference error_code_db in ac_data_repo.json for all brands.
Mitsubishi — P8 Comm Error Repair | P8 = indoor/outdoor comm fault. Check wiring + board. | MSZ/MXZ/MUZ series | N/A | N/A | 185 | 310 | 525 | 1.0–2.5 | Mini-Split | P8: 90% of time it's loose terminal at outdoor unit (S1/S2/S3). Check wiring first — saves board cost.
LG — CH05 Comm Error Repair | CH05 = indoor/outdoor comm fault. Most common LG Houston call. | LSN/LSXS/LMNS series | N/A | N/A | 185 | 310 | 525 | 1.0–2.5 | Mini-Split | Check S1/S2 communication wiring at indoor terminal strip. Loose wire is #1 cause.
LG — CH21 High Pressure Repair | CH21 = high pressure. Fan fault, dirty coil, or overcharge. | All LG mini-split series | N/A | N/A | 195 | 325 | 545 | 1.0–2.5 | Mini-Split | Check outdoor fan motor first, then coil cleanliness, then refrigerant charge. Houston summer heat makes this more frequent.
Gree — E1/E6 Error Repair | E1 = high pressure. E6 = comm error. Common on budget Gree DIY installs. | Gree LIVS, LIVH, SAPRO series | N/A | N/A | 175 | 295 | 485 | 1.0–2.5 | Mini-Split | E6: check communication wiring — common on DIY installs with incorrect wiring.
MrCool DIY — P6 Repair | P6 = low pressure/refrigerant protection. #1 MrCool call in Houston. | MrCool DIY and Signature series | N/A | N/A | 195 | 335 | 565 | 1.0–2.5 | Mini-Split | Check pre-charged lineset connection first — most common DIY failure point. Then check charge with gauges.
Pioneer — E4/E5 Error Repair | E4 = comm error. E5 = high pressure. Common Pioneer codes. | Pioneer Diamante/Hyper Heat series | N/A | N/A | 175 | 295 | 485 | 1.0–2.5 | Mini-Split | Pioneer uses Gree internals — cross-reference Gree error code logic if Pioneer chart is unavailable.
Bosch — Error Code Repair | Bosch mini-split (Climate 5000 series). Increasing Houston presence. | Bosch Climate 5000 series | N/A | N/A | 185 | 315 | 535 | 1.0–2.5 | Mini-Split | Bosch mini-splits are growing in Houston market. Error code reference: bosch-climate.com service portal.
⚠ All prices = customer-facing installed (parts+labor). Wholesale=40–60% of retail.

## 11. DUCTWORK & MISC
DUCTWORK, CONDENSATE & MISCELLANEOUS — Houston Installed 2025–2026
PART / SERVICE | DESCRIPTION | SPECS / NOTES | PART COST (Wholesale) | PART COST (Retail) | INSTALLED (Min) | INSTALLED (Typical) | INSTALLED (Max) | LABOR (Hrs) | CATEGORY | MARK'S NOTES
Ductwork Section Repair | Seal/repair accessible duct section. Mastic + foil tape. | Mastic sealant + UL-listed foil tape | $25–$75 | $35–$95 | 250 | 375 | 550 | 1.0–2.5 | Ductwork | MASTIC = correct sealant. Duct tape is NOT approved — fails within 2 years in Houston attic heat. Bill attic premium in summer.
Flex Duct — Section Replace (per ft) | Replace damaged or kinked flex duct. Per linear foot installed. | R-6 or R-8 insulated flex, 8"–14" dia | $3.5–$6.5 | $5.5–$10 | 28 | 42 | 65 | 0.3–0.5 | Ductwork | Kinked flex = severe airflow restriction = low delta-T that mimics low charge. Check all duct runs before touching refrigerant.
Full Duct System Replacement | Complete duct replacement. Attic flex duct typical Houston. | Full system, 1,500–2,500 sq ft | N/A | N/A | 3500 | 5500 | 8500 | 12–20 | Ductwork | Full replacement done alongside system replacement. Conduct duct leakage test before/after. Houston target: <10% leakage.
Supply Register Replace | Replace damaged or broken supply register. | Stamped steel, painted, various sizes | $8–$22 | $14–$38 | 45 | 75 | 115 | 0.3–0.5 | Ductwork | Check all registers on delta-T calls — closed or blocked register causes airflow restriction that mimics low charge.
Return Air Grille Replace | Replace return air grille. Filter grille or plain. | Metal return grille, standard sizes | $12–$35 | $20–$55 | 55 | 90 | 135 | 0.3–0.5 | Ductwork | Blocked return = low airflow = coil freeze. Common source: furniture pushed against return register.
Condensate Pump | Electric pump for systems where gravity drain is not possible. | 115V condensate pump, 3–4 gph | $35–$75 | $55–$130 | 190 | 285 | 420 | 0.75–1.25 | Misc | Houston: most systems are attic gravity-drain. Pumps used on split-level or rare basement systems.
Secondary Drain Pan Replace | Replace rusted secondary emergency drain pan under air handler. | PVC or galvanized steel secondary pan | $45–$110 | $80–$185 | 280 | 445 | 680 | 1.0–2.0 | Misc | Rusty secondary pan in Houston attic = imminent ceiling water damage. Replace immediately if rusted through. Install float switch if not present.
Refrigerant Line Insulation | Replace or add foam insulation on suction line. | 3/4" or 7/8" ID foam insulation | $3–$8 | $5–$12 | 85 | 145 | 225 | 0.75–1.5 | Misc | Any exposed suction line without insulation sweats and drips in Houston summer. Check insulation on every service call.
Outdoor Unit Pad — Replace | Concrete or composite equipment pad for outdoor unit leveling. | 16x16" concrete or composite pad | $15–$40 | $25–$65 | 95 | 155 | 235 | 0.5–1.0 | Misc | Houston clay soil heaves. Unit tilting >5° = oil return issue in compressor. Re-level and install proper pad.
Mini-Split Wall Sleeve / Lineset Cover | Decorative lineset cover for exposed mini-split lineset on exterior wall. | PVC lineset cover, 3" or 4.5" wide, per ft | $5–$12 | $8–$20 | 45 | 80 | 130 | 0.5–1.0 | Misc | Houston UV degrades exposed lineset insulation in 3–5 years. Lineset cover protects insulation and looks professional.
⚠ All prices = customer-facing installed (parts+labor). Wholesale=40–60% of retail.

## 12. FULL SYSTEM REPLACE
FULL SYSTEM REPLACEMENT — Houston TX Installed Pricing 2026 (Equipment + Labor + Refrigerant + Basic Materials)
BRAND | TIER | SERIES | SEER2 RATING | REFRIGERANT | TONNAGE | INSTALLED (Budget/Low) | INSTALLED (Typical) | INSTALLED (Premium/High) | FEATURES | HOUSTON NOTES | MARK'S VERDICT
Goodman / Amana | Budget | GSX/GSXN / ASX (Entry) | 14–15 | R-410A | 1.5 | 3500 | 4200 | 5200 | Single-stage, piston, basic warranty | Manufactured in Waller TX — fastest parts availability in Houston. Most affordable name-brand. New construction staple. | Solid unit for rental properties and budget installs. Parts always at Johnstone same day.
Goodman / Amana | Budget | GSX/GSXN / ASX (Entry) | 14–15 | R-410A | 2.0 | 3800 | 4500 | 5600 | Single-stage, piston | Most common Goodman size in Houston rental properties. | Best value for landlords and investors. Not the most efficient but bulletproof and cheap to repair.
Goodman / Amana | Budget | GSX/GSXN / ASX (Entry) | 14–15 | R-410A | 2.5 | 4000 | 4900 | 6100 | Single-stage, piston | Highest volume Houston residential replacement tonnage. | My go-to recommendation for homeowners on a budget who just need cooling. Does the job.
Goodman / Amana | Budget | GSX/GSXN / ASX (Entry) | 14–15 | R-410A | 3.0 | 4400 | 5300 | 6600 | Single-stage, piston | Standard builder-grade Houston replacement. | Goodman 3T is probably the single most common replacement unit I install in a given month.
Goodman / Amana | Budget | GSX/GSXN / ASX (Entry) | 14–15 | R-410A | 4.0 | 5000 | 6000 | 7500 | Single-stage, piston | For larger Houston homes 2,000–2,800 sq ft. | At 4T I start pushing homeowners toward mid-tier — efficiency savings start to matter at larger systems.
Goodman / Amana | Budget | GSX/GSXN / ASX (Entry) | 14–15 | R-410A | 5.0 | 5500 | 6700 | 8400 | Single-stage, piston | For 2,800+ sq ft homes. | 5T single-stage is a lot of on/off cycling. Humidity control suffers. Push two-stage at this size.
Bryant / Payne | Mid | Legacy / Preferred | 15–17 | R-410A | 2.5 | 5200 | 6500 | 8000 | Single or two-stage, TXV on Preferred | Same internals as Carrier. Strong dealer network. Good parts availability at Carrier Enterprise. | Bryant Performance/Preferred is a great sweet spot — better than Goodman, less than Carrier. Reliable.
American Standard / Ruud | Mid | Gold / Achiever | 15–17 | R-410A | 2.5 | 5200 | 6500 | 8000 | Single or two-stage, TXV | Identical to Trane/Rheem internally. Strong Houston presence. | Same unit as Trane XR/Rheem Select internally. Solid choice. Parts interchangeable with Trane.
Rheem / Ruud | Mid | Select / Achiever | 15–17 | R-410A | 3.0 | 5500 | 7000 | 8800 | Single or two-stage, TXV | EcoNet smart thermostat compatible. | Rheem is underrated in Houston. EcoNet app is good for homeowners who want remote monitoring.
York / Heil / Coleman | Mid | LX / QuietComfort / Echelon | 14–16 | R-410A | 3.0 | 5300 | 6600 | 8400 | Single-stage, piston or TXV | Johnson Controls family. ICP distributor parts. | York is solid. Parts are sometimes a day behind Carrier/Goodman on same-day pull but improving.
Daikin | Mid | DN / DX Series | 14–20 | R-410A | 3.0 | 5500 | 7200 | 9200 | Single or two-stage, TXV on DX | Manufactured in Waller TX. Growing market share rapidly. | Daikin is my pick for mid-tier today. Local manufacturing means parts are fast. DX17 gives great efficiency.
Carrier | Premium | Performance (2-stage) | 15–17 | R-410A | 3.0 | 7000 | 9000 | 11500 | Two-stage, TXV, Hybrid Heat capable | Carrier Performance is the most popular premium choice in Houston. Infinity thermostat optional. | If homeowner has money, Performance series is the right move. Better humidity control than entry.
Carrier | Premium — Variable | Infinity (variable speed) | 17–24 | R-410A | 3.0 | 10500 | 13500 | 17000 | Variable speed, EEV, Infinity system | Full communicating system. Highest efficiency. 10-yr parts + labor warranty option. | Infinity is the best residential system I've seen in 20 years. Humidity control in Houston is night and day vs single-stage.
Trane | Premium | XL Series (2-stage) | 16–18 | R-410A | 3.0 | 7200 | 9200 | 11800 | Two-stage, TXV, Nexia compatible | It's hard to stop a Trane. Very strong reputation in Houston premium market. | Trane XL is bulletproof. Slightly more expensive than Carrier but the brand value resonates with homeowners.
Trane | Premium — Variable | XV Series (variable speed) | 20–22 | R-410A | 3.0 | 11000 | 14000 | 18000 | Variable speed, EEV, ComfortLink II | Top-of-line residential. Best humidity control in the market. | If I'm replacing my own house — it's a Trane XV or Carrier Infinity. Both are exceptional.
Lennox | Premium | Elite (2-stage) | 16–18 | R-410A | 3.0 | 7000 | 9000 | 11500 | Two-stage, TXV, iHarmony zoning | Headquartered in TX. Strong Texas distributor network. Richardson TX manufacturing. | Elite is competitive with Carrier/Trane at similar price. Lennox parts availability is excellent in Texas.
Lennox | Premium — Variable | Signature / SL28XCV | 20–28 | R-454B (2025+) | 3.0 | 11500 | 15000 | 19500 | Variable speed, R-454B/R-32, highest SEER in market | 28 SEER2 is the highest in residential. First Lennox R-454B units arriving in Houston 2025. | SL28XCV is the most efficient residential AC made. Overkill for most homeowners but makes sense in all-electric homes with solar.
Goodman / Amana | Budget HP | GSZH / ASHP | 14–16 | R-410A | 3.0 | 4800 | 5900 | 7400 | Single-stage heat pump + air handler | Heat pump for Houston is great — mild winters mean HP handles nearly 100% of heating. | Heat pump makes total sense in Houston. Heats for 1/3 the cost of gas on mild winter days.
Carrier | Premium HP | Performance / Infinity HP | 17–24 | R-410A | 3.0 | 9000 | 12500 | 16500 | Variable speed heat pump | Infinity variable-speed HP has the best dehumidification of any system in Houston. | Dual fuel setup (HP + gas furnace) is the ultimate Houston system — HP for efficiency, gas for the rare freeze. But at $15,000+ it's a hard sell.
Mitsubishi / Daikin | Mini-Split — Single Zone | M-Series / SkyAir | 20–26 | R-410A | 9K–24K BTU | 2500 | 3800 | 5500 | Variable speed, EEV, remote/wifi control | No ductwork needed. Houston additions, sunrooms, garages, offices. | Mini-split is the right answer for any room addition or garage in Houston. Quietest, most efficient option for single-zone.
LG / Samsung | Mini-Split — Single Zone | Multi + Art Cool | 18–22 | R-410A | 9K–24K BTU | 2400 | 3600 | 5200 | Variable speed, inverter, wifi | Growing Houston market share. Samsung 360 cassette popular in commercial adjacent. | LG Art Cool is visually clean on the wall — helps sell to design-conscious homeowners. Good warranty.
Mitsubishi / Daikin | Mini-Split — Multi Zone | MXZ / SkyAir Multi | 18–26 | R-410A | 2–5 zones | 5500 | 8500 | 14000 | 1 outdoor, 2–5 indoor units | Best solution for full house zoning without ductwork. Common in Houston room additions. | Multi-zone mini-split is getting very competitive with full ducted system on a whole-house basis. Worth presenting as an option.
⚠ Full system replacement = outdoor unit + indoor coil/air handler + installation labor + refrigerant + basic electrical. EXCLUDES: ductwork modification, new thermostat, permit fees ($50–200), crane fees (if needed). Add $2,000–7,000 for ductwork replacement. Premium pricing reflects high-efficiency variable-speed systems.
📌 Houston off-season (Nov–Feb) pricing typically 15–20% lower than peak summer. Lock in equipment contracts in winter for summer installs.

## 13. FAULT CARDS
FAULT CARD DIAGNOSTIC ESTIMATES — All 19 Cards · Houston Frequency · Installed Pricing 2025–2026
CARD # | FAULT NAME | HOUSTON FREQ % | PRIMARY PARTS | OPTIONAL PARTS | LABOR (Hrs) | ESTIMATE (Min) | ESTIMATE (Typical) | ESTIMATE (Max) | PHASE | DIFFICULTY | MARK'S FIELD NOTES
1 | Capacitor Failure | 18% | Dual Run Capacitor | Contactor | 0.4–0.75 | 175 | 245 | 330 | Phase 1 | Easy | #1 summer call. Always check contactor while panel is open. Recommend combo replacement if contactor shows ANY pitting. Stock 35/5, 40/5, 45/5, 50/5, 55/5 MFD in both 370V and 440V.
2 | Dirty Filter | 12% | 1" Filter or Media Filter | Drain Flush Tablet | 0.15–0.25 | 18 | 35 | 120 | Phase 1 | Trivial | Fastest resolution. Photo of clogged filter = instant homeowner trust. Always add drain flush tablet — filter clog causes condensate backup.
3 | Contactor Failure | 7% | Contactor 2-pole | Dual Run Capacitor | 0.4–0.75 | 175 | 235 | 330 | Phase 1 | Easy | Pitting on contact face = definitive failure. Voltage reading confirms. Always check capacitor simultaneously.
4 | Blower Motor Failure | 4% | PSC or ECM Blower Motor | Run Capacitor (single) | 1.5–3.0 | 325 | 550 | 900 | Phase 1 | Moderate | ECM requires exact replacement. PSC more flexible. Check blower wheel for debris while motor is out — always.
5 | Drain Clog | 20% | Drain Flush Chemical + Pan Tablet | Drain Pan Full Clean | 0.5–1.25 | 120 | 185 | 280 | Phase 1 | Easy | #1 Houston call by volume. High humidity = algae weekly. Always leave pan tablet. Recommend quarterly flush contract.
6 | Wiring Fault | 2% | Wiring / Terminal Repair | Fuse Replacement | 0.75–2.0 | 145 | 230 | 400 | Phase 1 | Moderate | Voltage drop >3V confirms. Burn marks on terminal = photo evidence for homeowner report.
7 | Control Board / Error Code | 3% | Control Board or Thermostat | Fuse | 0.75–1.75 | 235 | 480 | 700 | Phase 1 | Moderate | Decode LED flash code first — routes directly to fault. Check board fuse before condemning board.
8 | Refrigerant Leak | 8% | Leak Search + UV Dye + R-410A + Recovery/Recharge | TXV or Evap Coil | 2.0–5.0 | 450 | 750 | 1900 | Phase 2 | Complex | Find the leak source — do NOT just recharge and leave. UV photo is homeowner evidence. Minor leak: $450–750. Evap coil leak: $950–1,900.
9 | Coil Freeze | 5% | Filter + Evap Coil Cleaning | R-410A per lb | 1.5–3.0 | 165 | 285 | 500 | Phase 1 | Moderate | Let coil thaw 1–3 hrs first. Root cause = dirty filter or low charge. Fix root cause, not just symptom.
10 | Compressor Failure | 4% | Compressor (by tonnage) | Recovery/Recharge + Refrigerant | 4.0–7.0 | 1100 | 1600 | 2500 | Tech Judgment | Major | Most expensive repair. If 8+ years old: present replacement vs repair with clear TCO comparison. RLA over nameplate = over-amping evidence.
11 | Ignitor / Flame Sensor | 3% | Hot Surface Ignitor + Flame Sensor | Furnace Control Board | 0.4–0.75 | 120 | 210 | 325 | Phase 1 | Easy | Clean flame sensor first with steel wool — saves $165 repair if it works. Photo of cracked ignitor = compelling evidence.
12 | Reversing Valve (Heat Pump) | 1% | Reversing Valve + Recovery/Recharge | R-410A per lb | 3.5–5.5 | 475 | 750 | 1100 | Phase 2 | Complex | Stuck in cooling = can cool not heat. Stuck in heating = opposite. Rare in Houston due to low heating demand.
13 | Ductwork Leak | 2% | Ductwork Section Repair | Flex Duct Section | 1.5–4.0 | 250 | 425 | 800 | Tech Judgment | Moderate | Attic work in Houston summer = premium billing. Schedule early morning. Mastic + foil tape only — duct tape is NOT approved.
14 | Dirty Coil (Condenser/Evap) | 6% | Condenser Coil Cleaning + Evap Coil Cleaning | Filter | 0.75–2.0 | 145 | 235 | 385 | Phase 2 | Easy-Moderate | YOLO photo strongest use case — dirty condenser is visible from outside. High discharge + high subcooling confirms. Best spring upsell.
15 | Piston Mismatch | 2% | Fixed Orifice Piston + Recovery/Recharge + R-410A | TXV Upgrade | 2.5–4.5 | 350 | 525 | 750 | Phase 2 | Moderate | Bore measurement vs nameplate tonnage confirms. Common after system swaps where matching piston was not installed.
16 | Loose Terminal | 2% | Terminal Clean + Retorque | Wiring Repair | 0.5–1.25 | 125 | 210 | 375 | Phase 2 | Easy-Moderate | Voltage drop >3V confirms. Point thermometer = hottest terminal = loose one. No part usually needed.
17 | Refrigerant Overcharge | 2% | Recovery/Recharge (remove excess) | None typically | 1.5–3.0 | 200 | 300 | 450 | Phase 2 | Moderate | High discharge + high subcooling (>18°F TXV). Do NOT add refrigerant — recover. Differentiate from dirty coil via photo.
18 | System Undersizing | 1% | N/A — leads to system replacement | None | 0.5–1.0 | 0 | 0 | 0 | Tech Judgment | Complex | No repair estimate — load calculation and full system replacement recommendation. Square footage + insulation + windows + Houston climate factor.
19 | Formicary Corrosion | 1% | Evaporator Coil (by tonnage) + UV Dye | New Lineset if contaminated | 3.5–6.0 | 950 | 1350 | 2050 | Phase 1 (visual) | Major | Green/white powder on evap coil face = formicary. Caused by formic acid from VOCs. Coil replacement required — cannot be patched.
⚠ Card #5 (Drain Clog) and Card #1 (Capacitor) account for 38% of all Houston HVAC service calls. Stock for these two on every truck and you'll handle the majority of summer calls. Card #10 (Compressor) is highest single-repair value ($1,100–$2,500).

## 14. BRAND REF
BRAND QUICK REFERENCE — All Houston HVAC Brands (2025–2026)
BRAND | PARENT CO. | SISTER BRANDS | TIER | SERIES | METERING DEVICE | COMPRESSOR TYPE | SEER2 | REFRIGERANT | HOUSTON PREVALENCE | TX MANUFACTURED? | PARTS SOURCE
Carrier | Carrier Global Corp. | Bryant, Payne | Entry | Comfort (24ACC) | Piston | Single-stage | 13.8–14.5 | R-410A | Very High | No | Carrier Enterprise, Johnstone Supply
Carrier | Carrier Global Corp. | Bryant, Payne | Mid | Performance (24ANA) | TXV | Two-stage | 15–17 | R-410A | Very High | No | Carrier Enterprise, Johnstone Supply
Carrier | Carrier Global Corp. | Bryant, Payne | Premium | Infinity (24VNA) | EEV | Variable speed | 17–24 | R-410A / R-454B (2025+) | Very High | No | Carrier Enterprise only
Bryant | Carrier Global Corp. | Carrier, Payne | Entry | Legacy (913S/LCA) | Piston | Single-stage | 14–14.5 | R-410A | High | No | Carrier Enterprise (same as Carrier)
Bryant | Carrier Global Corp. | Carrier, Payne | Mid | Preferred (127B) | TXV | Two-stage | 15–17 | R-410A | High | No | Carrier Enterprise (same as Carrier)
Bryant | Carrier Global Corp. | Carrier, Payne | Premium | Evolution (180B) | EEV | Variable speed | 17–24 | R-410A | High | No | Carrier Enterprise only
Payne | Carrier Global Corp. | Carrier, Bryant | Entry | PA14/PA16 | Piston | Single-stage | 14–16 | R-410A | Medium-Low | No | Carrier Enterprise (same as Carrier)
Trane | Trane Technologies | American Standard | Entry | XR (4TTR/4TTB) | Piston | Single-stage | 14.8–15 | R-410A | Very High | No | Trane Supply, Johnstone Supply
Trane | Trane Technologies | American Standard | Mid | XL (4TTX) | TXV | Two-stage | 16–18 | R-410A | Very High | No | Trane Supply
Trane | Trane Technologies | American Standard | Premium | XV (4TVA/XV20) | EEV | Variable speed | 20–22 | R-410A / R-454B (2025+) | Very High | No | Trane Supply only
American Standard | Trane Technologies | Trane | Entry–Premium | Gold / Silver / Platinum | Piston/TXV/EEV | Single/Two/Variable | 14.3–22 | R-410A | High | No | Trane Supply (identical to Trane)
Lennox | Lennox International | Heil, Armstrong | Entry | Merit (13ACX/ML14) | Piston | Single-stage | 14.3–15 | R-410A | High | Yes — Richardson TX | Lennox Parts Plus, Johnstone
Lennox | Lennox International | Heil, Armstrong | Mid | Elite (16ACX/EL16) | TXV | Two-stage | 16–18 | R-410A | High | Yes — Richardson TX | Lennox Parts Plus
Lennox | Lennox International | Heil, Armstrong | Premium | Signature/SL28XCV | EEV | Variable speed | 20–28 | R-32 / R-454B (2025+) | High | Yes — Richardson TX | Lennox Parts Plus only
Goodman | Daikin Industries | Amana, Daikin | Entry | GSX/GSXN | Piston | Single-stage | 14–15 | R-410A | Very High | Yes — Waller TX | Johnstone Supply, Wesco
Goodman | Daikin Industries | Amana, Daikin | Mid | GSXC16/GSXC18 | TXV | Two-stage | 16–18 | R-410A | Very High | Yes — Waller TX | Johnstone Supply
Goodman | Daikin Industries | Amana, Daikin | Premium | GSXV9 | EEV | Variable speed | 18–22.5 | R-410A / R-454B (2025+) | Very High | Yes — Waller TX | Johnstone Supply
Amana | Daikin Industries | Goodman, Daikin | Entry–Premium | ASX/ASXC/ASXV | Piston/TXV/EEV | Single/Two/Variable | 14–22.5 | R-410A | Medium | Yes — Waller TX | Same as Goodman — identical unit
Daikin | Daikin Industries (Japan) | Goodman, Amana | Entry | DN14/DN16 | Piston | Single-stage | 14–16 | R-410A | Medium-High | Yes — Waller TX | Johnstone Supply, Wesco
Daikin | Daikin Industries (Japan) | Goodman, Amana | Mid–Premium | DX17/DX20/Daikin Fit | TXV/EEV | Two-stage/Variable | 17–24.5 | R-410A | Medium-High | Yes — Waller TX | Daikin distributor, Johnstone
Rheem | Paloma Co. / Rheem Mfg. | Ruud | Entry–Premium | Select/Achiever/Prestige | Piston/TXV/EEV | Single/Two/Variable | 14–22.5 | R-410A / R-454B (2025+) | High | No | Johnstone Supply, Wesco
Ruud | Rheem Manufacturing | Rheem | Entry–Premium | EcoNet Select/Achiever/Ultra | Piston/TXV/EEV | Single/Two/Variable | 14–22.5 | R-410A | Medium | No | Identical to Rheem — same parts
York | Johnson Controls | Coleman, Heil, Luxaire | Entry–Premium | LX/Affinity/YXV | Piston/TXV/EEV | Single/Two/Variable | 14–21 | R-410A | Medium-High | No | ICP distributor, Johnstone
Heil | Johnson Controls (ICP) | York, Coleman, Luxaire | Entry–Mid | QuietComfort / QCD | Piston/TXV | Single/Two-stage | 14–18 | R-410A | Medium | No | ICP distributor, Johnstone
Coleman | Johnson Controls (York) | York, Heil, Luxaire | Entry–Mid | Echelon / Echelon Deluxe | Piston/TXV | Single/Two-stage | 14–18 | R-410A | Medium-Low | No | ICP distributor, Johnstone
Mitsubishi Electric | Mitsubishi Electric Corp. | None | Mini-Split | M-Series/MSZ, Hyper-Heat | EEV | Variable speed inverter | 15–26 | R-410A | Medium-Low | No | Mitsubishi distributor only
Daikin Mini-Split | Daikin Industries | None | Mini-Split | SkyAir/FT series | EEV | Variable speed inverter | 17–24.5 | R-410A | Medium-High | Yes — Waller TX | Daikin distributor
LG | LG Electronics | None | Mini-Split | LSN/LSXS/LMNS series | EEV | Variable speed inverter | 18–22 | R-410A | Medium-Low | No | LG distributor, HVACDirect
Samsung | Samsung Electronics | None | Mini-Split | AR/AW series | EEV | Variable speed inverter | 17–21 | R-410A | Medium-Low | No | Samsung distributor, HVACDirect
Gree | Gree Electric Appliances | None | Mini-Split | LIVS/LIVH/SAPRO | EEV | Variable speed inverter | 16–21 | R-410A | Low-Medium | No | HVACDirect, wholesale distributors
Pioneer | Pioneer (US distrib.) | None | Mini-Split | Diamante/Hyper Heat | EEV | Variable speed inverter | 16–20 | R-410A | Low-Medium | No | HVACDirect, Pioneer wholesaler
MrCool | MrCool LLC | None | Mini-Split | DIY / Signature | EEV | Variable speed inverter | 16–20 | R-410A | Low-Medium (growing) | No | Home Depot, HVACDirect
Bosch | Bosch Thermotechnology | None | Mini-Split | Climate 5000 series | EEV | Variable speed inverter | 16–22 | R-410A | Low (growing) | No | Bosch-climate.com, distributors
📌 Houston market: Carrier, Trane, Goodman are the top 3 brands by install volume. Goodman/Daikin manufactured in Waller TX gives fastest Houston parts availability. R-454B/R-32 are A2L refrigerants — require certified equipment. Verify current refrigerant when servicing 2025+ units.